## 0926_2004_5b
building type | scenario | results directory | city | net site energy | total building area | eui | unmet hours during heating | unmet hours during cooling | unmet hours during occupied heating | unmet hours during occupied cooling | fuel electricity | fuel natural gas | fuel additional fuel | fuel district cooling | fuel district heating | annual peak electric demand | end use interior lighting | end use exterior lighting | end use interior equipment | end use exterior equipment | end use water systems | end use refrigeration | end use heating | end use cooling | end use fans | end use pumps | end use heat rejection | end use humidification | end use heat recovery | end use generators | sum of end use errors as fraction of total consumpiton | end use electricity interior lighting | end use electricity exterior lighting | end use electricity interior equipment | end use electricity exterior equipment | end use electricity water systems | end use electricity refrigeration | end use electricity heating | end use electricity cooling | end use electricity fans | end use electricity pumps | end use electricity heat rejection | end use electricity humidification | end use electricity heat recovery | end use electricity generators | end use natural gas interior lighting | end use natural gas exterior lighting | end use natural gas interior equipment | end use natural gas exterior equipment | end use natural gas water systems | end use natural gas refrigeration | end use natural gas heating | end use natural gas cooling | end use natural gas fans | end use natural gas pumps | end use natural gas heat rejection | end use natural gas humidification | end use natural gas heat recovery | end use natural gas generators | zone lights total heating energy annual | electric equipment total heating energy annual | gas equipment total heating energy annual | zone people sensible heating energy annual | zone mechanical ventilation cooling load increase energy annual | zone infiltration sensible heat gain energy annual | ground heat gain | ext wall heat gain | surface window heat gain energy annual | ext roof heat gain | zone infiltration sensible heat loss energy annual | zone mechanical ventilation heating load increase energy annual | ground heat loss | ext wall heat loss | surface window heat loss energy annual | ext roof heat loss
SecondarySchool | 0 - Prototype | run/Prototype Row B/datapoint_59c942e553ff6b03c8620174 | Boise Air Terminal Uo | 15226100 | 210887 | 72.2003 | 621.25 | 1969.25 | 1.5 | 89.25 | 9720800 | 5505260 | 0 | 0 | 0 | 1175.45 | 3189060 | 209022 | 2834710 | 0 | 509186 | 84270.4 | 4471960 | 1676700 | 2032640 | 60120 | 0 | 0 | 158371 | 0 |  | 934622 | 61258.3 | 676753 | 0 | 419.444 | 24697.2 | 0 | 491392 | 595708 | 17619.4 | 0 | 0 | 46413.9 | 0 | 0 | 0 | 5256.38 | 0 | 5078.53 | 0 | 44728.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3189070 | 2204750 | 157660 | 2711290 | 654732 | 20553.6 | 283352 | 910661 | 2556670 | 1643270 | 370205 | 632408 | 1129730 | 1243200 | 1469050 | 2335910
SecondarySchool | 1 - Prototype-NewHvac | run/Prototype Row B/datapoint_59c942ed53ff6b03c8620184 | Boise Air Terminal Uo | 15823600 | 210887 | 75.0338 | 536.5 | 2042.5 | 18.5 | 296.75 | 10202500 | 5621110 | 0 | 0 | 0 | 926.547 | 3189060 | 209022 | 2834710 | 0 | 509859 | 84460 | 4587150 | 1691430 | 1830340 | 337205 | 79417.6 | 0 | 470961 | 0 |  | 934622 | 61258.3 | 676753 | 0 | 419.444 | 24752.8 | 0 | 495708 | 536419 | 98825 | 23275 | 0 | 138025 | 0 | 0 | 0 | 5256.38 | 0 | 5085.26 | 0 | 45880.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3189070 | 2204750 | 157660 | 2756970 | 497063 | 24494.4 | 393005 | 914757 | 2581620 | 1661490 | 361372 | 872298 | 961851 | 1235420 | 1445630 | 2307040
SecondarySchool | 2 - Prototype-NewHvacLoadsConstSch | run/Prototype Row B/datapoint_59c942f553ff6b03c8620194 | Boise Air Terminal Uo | 16415100 | 210887 | 77.8383 | 658 | 1744.75 | 38.5 | 246.5 | 10329600 | 6085470 | 0 | 0 | 0 | 921.225 | 3189060 | 548274 | 2838730 | 0 | 423267 | 84327.3 | 5138100 | 1590670 | 1756770 | 317651 | 76223.5 | 0 | 451976 | 0 |  | 934622 | 160683 | 677931 | 0 | 419.444 | 24713.9 | 0 | 466181 | 514858 | 93094.4 | 22338.9 | 0 | 132461 | 0 | 0 | 0 | 5256.38 | 0 | 4219.17 | 0 | 51390.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3189070 | 2204950 | 157660 | 2773620 | 491970 | 47343.9 | 199747 | 918287 | 2595460 | 1668300 | 506863 | 1137650 | 1430010 | 1226690 | 1417410 | 2287940
SecondarySchool | 3b - Typical-Bar-Sliced | run/Prototype Row B/datapoint_59c9430753ff6b03c86201a4 | Boise Air Terminal Uo | 20005600 | 210887 | 94.8643 | 1084 | 2507.75 | 9.25 | 285.25 | 10531700 | 9473990 | 0 | 0 | 0 | 916.936 | 3189050 | 535763 | 2837440 | 0 | 392302 | 0 | 8557390 | 1549790 | 2165250 | 311329 | 73996.1 | 0 | 393335 | 0 |  | 934619 | 157017 | 677900 | 0 | 0 | 0 | 13.8889 | 454200 | 634572 | 91241.7 | 21686.1 | 0 | 115275 | 0 | 0 | 0 | 5244.53 | 0 | 3923.77 | 0 | 85589.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3189050 | 2204930 | 157305 | 2742070 | 394217 | 39400.5 | 199111 | 807587 | 1920050 | 1226350 | 418150 | 1781890 | 1353091 | 1089670 | 986109 | 1788280
SecondarySchool | 4b - Typical-Bar-Blend | run/Prototype Row B/datapoint_59c9431053ff6b03c86201b4 | Boise Air Terminal Uo | 17358600 | 210887 | 82.3124 | 524.25 | 453.25 | 10.25 | 61.75 | 9974930 | 7383680 | 0 | 0 | 0 | 885.106 | 3189050 | 535763 | 2837440 | 0 | 392292 | 0 | 6467040 | 1425890 | 1852320 | 287985 | 76147.6 | 0 | 294695 | 0 |  | 934619 | 157017 | 677900 | 0 | 0 | 0 | 0 | 417886 | 542861 | 84400 | 22316.7 | 0 | 86366.7 | 0 | 0 | 0 | 5244.53 | 0 | 3923.68 | 0 | 64682.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3189050 | 2204930 | 157305 | 2810830 | 326279 | 49064.8 | 107607 | 808286 | 1925770 | 1232654 | 480939 | 1528630 | 1360430 | 1099230 | 1013090 | 1802400
SecondarySchool | 4c - Typical-Urban-Blend | run/Prototype Row B/datapoint_59c9432b53ff6b03c86201c6 | Boise Air Terminal Uo | 17107200 | 256242 | 66.7618 | 403.25 | 271 | 2 | 12.75 | 10269900 | 6837300 | 0 | 0 | 0 | 1026.67 | 3874900 | 535763 | 3447680 | 0 | 392292 | 0 | 5807890 | 1349800 | 1056100 | 268725 | 79237.5 | 0 | 294771 | 0 |  | 1135620 | 157017 | 823694 | 0 | 0 | 0 | 0 | 395586 | 309511 | 78755.6 | 23222.2 | 0 | 86388.9 | 0 | 0 | 0 | 6372.46 | 0 | 3923.68 | 0 | 58090.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3874910 | 2679130 | 191136 | 3304310 | 377559 | 49287.1 | 24254 | 928896 | 1898220 | 1464240 | 581080 | 1913130 | 2037560 | 1296940 | 1049100 | 2182880
SecondarySchool | 4d - Prototype-Prototype-Blend | run/Prototype Row B/datapoint_59c991be45b421004abe3aa7 | Boise Air Terminal Uo | 15775800 | 210887 | 74.807 | 412.75 | 454.25 | 5.5 | 49 | 9909460 | 5866330 | 0 | 0 | 0 | 894.492 | 3189060 | 548274 | 2838730 | 0 | 423257 | 78972.1 | 4918970 | 1427490 | 1636070 | 286336 | 74157.2 | 0 | 354446 | 0 |  | 934622 | 160683 | 677931 | 0 | 419.444 | 23144.4 | 0 | 418356 | 479486 | 83916.7 | 21733.3 | 0 | 103878 | 0 | 0 | 0 | 5256.38 | 0 | 4219.07 | 0 | 49199.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3189070 | 2204950 | 157660 | 2806180 | 511073 | 48637.9 | 173124 | 918779 | 2593910 | 1662830 | 544247 | 1034980 | 1396710 | 1225670 | 1418510 | 2286260
| bonus - 0 ot 2 error as single step | [15 empty] | 0 | 339252 | 4020 | 0 | 85919 | 56.9 | 666140 | 86030 | 275870 | 257531 | 76223.5 | 0 | 293605 | 0 | 13.69%
SecondarySchool | 0 - Prototype¦1 - Prototype-NewHvac |  | Boise Air Terminal Uo | 597500 | 0 | 2.8335 | 84.75 | 73.25 | 17 | 207.5 | 481700 | 115850 | 0 | 0 | 0 | 248.903 | 0% | 0% | 0% | 0% | 0.00442% | 0.001245% | 0.7565% | 0.09674% | 1.329% | 1.82% | 0.5216% | 0% | 2.053% | 0% | 6.582% | 0 | 0 | 0 | 0 | 0 | 55.6 | 0 | 4316 | 59289 | 81205.6 | 23275 | 0 | 91611.1 | 0 | 0 | 0 | 0 | 0 | 6.73 | 0 | 1152.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45680 | 157669 | 3940.8 | 109653 | 4096 | 24950 | 18220 | 8833 | 239890 | 167879 | 7780 | 23420 | 28870
SecondarySchool | 1 - Prototype-NewHvac¦2 - Prototype-NewHvacLoadsConstSch |  | Boise Air Terminal Uo | 591500 | 0 | 2.8045 | 121.5 | 297.75 | 20 | 50.25 | 127100 | 464360 | 0 | 0 | 0 | 5.322 | 0% | 2.144% | 0.02541% | 0% | 0.5472% | 0.0008386% | 3.482% | 0.6368% | 0.4649% | 0.1236% | 0.02019% | 0% | 0.12% | 0% | 7.565% | 0 | 99424.7 | 1178 | 0 | 0 | 38.9 | 0 | 29527 | 21561 | 5730.6 | 936.1 | 0 | 5564 | 0 | 0 | 0 | 0 | 0 | 866.09 | 0 | 5510.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 16650 | 5093 | 22849.5 | 193258 | 3530 | 13840 | 6810 | 145491 | 265352 | 468159 | 8730 | 28220 | 19100
SecondarySchool | 2 - Prototype-NewHvacLoadsConstSch¦3b - Typical-Bar-Sliced |  | Boise Air Terminal Uo | 3590500 | 0 | 17.026 | 426 | 763 | 29.25 | 38.75 | 202100 | 3388520 | 0 | 0 | 0 | 4.289 | 6.092e-07 | 0.07622% | 0.007859% | 0% | 0.1886% | 0.5137% | 20.83% | 0.249% | 2.488% | 0.03851% | 0.01357% | 0% | 0.3572% | 0% | 24.76% | 3 | 3666 | 31 | 0 | 419.444 | 24713.9 | 13.8889 | 11981 | 119714 | 1852.7 | 652.8 | 0 | 17186 | 0 | 0 | 0 | 11.85 | 0 | 295.4 | 0 | 34199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 355 | 31550 | 97753 | 7943.4 | 636 | 110700 | 675410 | 441950 | 88713 | 644240 | 76919 | 137020 | 431301 | 499660
SecondarySchool | 2 - Prototype-NewHvacLoadsConstSch¦4b - Typical-Bar-Blend |  | Boise Air Terminal Uo | 943500 | 0 | 4.4741 | 133.75 | 1291.5 | 28.25 | 184.75 | 354670 | 1298210 | 0 | 0 | 0 | 36.119 | 6.092e-07 | 0.07622% | 0.007859% | 0% | 0.1887% | 0.5137% | 8.096% | 1.004% | 0.5821% | 0.1807% | 0.0004624% | 0% | 0.9581% | 0% | 11.61% | 3 | 3666 | 31 | 0 | 419.444 | 24713.9 | 0 | 48295 | 28003 | 8694.4 | 22.2 | 0 | 46094.3 | 0 | 0 | 0 | 11.85 | 0 | 295.49 | 0 | 13292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 355 | 37210 | 165691 | 1720.9 | 92140 | 110001 | 669690 | 435646 | 25924 | 390980 | 69580 | 127460 | 404320 | 485540
SecondarySchool | 2 - Prototype-NewHvacLoadsConstSch¦4c - Typical-Urban-Blend |  | Boise Air Terminal Uo | 692100 | 45355 | 11.0765 | 254.75 | 1473.75 | 36.5 | 233.75 | 59700 | 751830 | 0 | 0 | 0 | 105.445 | 4.178% | 0.07622% | 3.71% | 0% | 0.1887% | 0.5137% | 4.08% | 1.467% | 4.268% | 0.2981% | 0.01836% | 0% | 0.9577% | 0% | 19.76% | 200998 | 3666 | 145763 | 0 | 419.444 | 24713.9 | 0 | 70595 | 205347 | 14338.8 | 883.3 | 0 | 46072.1 | 0 | 0 | 0 | 1116.08 | 0 | 295.49 | 0 | 6699.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 685840 | 474180 | 33476 | 530690 | 114411 | 1943.2 | 175493 | 10609 | 697240 | 204060 | 74217 | 775480 | 607550 | 70250 | 368310 | 105060
SecondarySchool | 2 - Prototype-NewHvacLoadsConstSch¦4d - Prototype-Prototype-Blend |  | Boise Air Terminal Uo | 639300 | 0 | 3.0313 | 245.25 | 1290.5 | 33 | 197.5 | 420140 | 219140 | 0 | 0 | 0 | 26.733 | 0% | 0% | 0% | 0% | 6.092e-07 | 0.03262% | 1.335% | 0.9941% | 0.7353% | 0.1908% | 0.01259% | 0% | 0.5941% | 0% | 3.895% | 0 | 0 | 0 | 0 | 0 | 1569.5 | 0 | 47825 | 35372 | 9177.7 | 605.6 | 0 | 28583 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 2191.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32560 | 19103 | 1294 | 26623 | 492 | 1550 | 5470 | 37384 | 102670 | 33300 | 1020 | 1100 | 1680
chart | [19 empty] | look at cause of heating change from 2 to 4b, heat gain from windows lower because of missing skylights
PrimarySchool | 0 - Prototype | run/Prototype Row B/datapoint_59c942e553ff6b03c8620175 | Boise Air Terminal Uo | 5799580 | 73958.8 | 78.4163 | 457.75 | 756.5 | 4.5 | 346.5 | 3598920 | 2200660 | 0 | 0 | 0 | 418.715 | 1151540 | 80393.8 | 1591590 | 0 | 126202 | 46395.6 | 1727970 | 467113 | 575856 | 3374.23 | 0 | 0 | 29145.4 | 0 |  | 337483 | 23561.1 | 364308 | 0 | 594.444 | 13597.2 | 0 | 136897 | 168767 | 988.889 | 0 | 0 | 8541.67 | 0 | 0 | 0 | 3485.89 | 0 | 1241.97 | 0 | 17283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1151540 | 1220250 | 104557 | 702834 | 216953 | 5241.34 | 180730 | 395051 | 1018890 | 899501 | 132416 | 338640 | 729806 | 534086 | 544936 | 1369980
PrimarySchool | 1 - Prototype-NewHvac | run/Prototype Row B/datapoint_59c942ed53ff6b03c8620185 | Boise Air Terminal Uo | 4732930 | 73958.8 | 63.9942 | 513.5 | 2551.5 | 0.5 | 27.75 | 3443020 | 1289910 | 0 | 0 | 0 | 386.462 | 1151540 | 80393.8 | 1591590 | 0 | 126211 | 46481 | 817634 | 415419 | 474193 | 85.3035 | 0 | 0 | 29382.3 | 0 |  | 337483 | 23561.1 | 364308 | 0 | 594.444 | 13622.2 | 125 | 121747 | 138972 | 25 | 0 | 0 | 8611.11 | 0 | 0 | 0 | 3485.89 | 0 | 1242.07 | 0 | 8173.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1151540 | 1220250 | 104557 | 693773 | 173249 | 3590.66 | 157610 | 390755 | 1002350 | 888922 | 137738 | 224850 | 919518 | 539948 | 560015 | 1390050
PrimarySchool | 2 - Prototype-NewHvacLoadsConstSch | run/Prototype Row B/datapoint_59c942f553ff6b03c8620195 | Boise Air Terminal Uo | 5043370 | 73958.8 | 68.1916 | 765 | 2068 | 1.25 | 25.5 | 3514130 | 1529250 | 0 | 0 | 0 | 379.583 | 1151540 | 175763 | 1591590 | 0 | 166920 | 46367.2 | 1018250 | 377004 | 487131 | 28.4345 | 0 | 0 | 28775.7 | 0 |  | 337483 | 51511.1 | 364308 | 0 | 594.444 | 13588.9 | 708.333 | 110489 | 142764 | 8.3333 | 0 | 0 | 8433.33 | 0 | 0 | 0 | 3485.89 | 0 | 1649.24 | 0 | 10160.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1151540 | 1220250 | 104557 | 698739 | 174998 | 9624.56 | 127361 | 393290 | 1011620 | 898178 | 188085 | 326476 | 1151740 | 532345 | 538396 | 1364030
PrimarySchool | 3b - Typical-Bar-Sliced | run/Prototype Row B/datapoint_59c9430753ff6b03c86201a5 | Boise Air Terminal Uo | 5457350 | 73989 | 73.759 | 2157 | 2253.5 | 0 | 65 | 3817380 | 1639970 | 0 | 0 | 0 | 395.16 | 1151990 | 175479 | 1591180 | 0 | 139661 | 0 | 1156140 | 436716 | 759789 | 28.4345 | 0 | 0 | 46386.2 | 0 |  | 337614 | 51427.8 | 364356 | 0 | 0 | 0 | 1105.56 | 127989 | 222672 | 8.3333 | 0 | 0 | 13594.4 | 0 | 0 | 0 | 3480.11 | 0 | 1396.88 | 0 | 11525.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1151990 | 1220440 | 104383 | 680032 | 162645 | 9459.55 | 267796 | 354081 | 902092 | 899665 | 173356 | 503348 | 1275230 | 490758 | 472848 | 1307520
PrimarySchool | 4b - Typical-Bar-Blend | run/Prototype Row B/datapoint_59c9431053ff6b03c86201b5 | Boise Air Terminal Uo | 5161830 | 73989 | 69.7649 | 885.25 | 530 | 3 | 88.25 | 3747890 | 1413940 | 0 | 0 | 0 | 373.554 | 1151990 | 175479 | 1591180 | 0 | 139651 | 0 | 927543 | 375146 | 719526 | 28.4345 | 0 | 0 | 81303.8 | 0 |  | 337614 | 51427.8 | 364356 | 0 | 0 | 0 | 350 | 109944 | 210872 | 8.3333 | 0 | 0 | 23827.8 | 0 | 0 | 0 | 3480.11 | 0 | 1396.78 | 0 | 9265.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1151990 | 1220440 | 104383 | 686851 | 134419 | 9561.58 | 271411 | 352596 | 899908 | 897322 | 180173 | 489321 | 1261340 | 490519 | 471552 | 1301670
PrimarySchool | 4c - Typical-Urban-Blend | run/Prototype Row B/datapoint_59c9432b53ff6b03c86201c7 | Boise Air Terminal Uo | 5110610 | 73963.6 | 69.0963 | 152.25 | 159.5 | 0 | 39 | 3375850 | 1734750 | 0 | 0 | 0 | 320.686 | 1151590 | 175479 | 1590620 | 0 | 139651 | 0 | 1247750 | 267265 | 538208 | 28.4345 | 0 | 0 | 0 | 0 |  | 337497 | 51427.8 | 364228 | 0 | 0 | 0 | 141.667 | 78327.8 | 157733 | 8.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 3478.88 | 0 | 1396.78 | 0 | 12475.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1151590 | 1220020 | 104348 | 698074 | 196288 | 9562.49 | 306174 | 391532 | 780896 | 887853 | 178933 | 333157 | 1306630 | 542430 | 411267 | 1292470
PrimarySchool | 4d - Prototype-Prototype-Blend | run/Prototype Row B/datapoint_59c991be45b421004abe3aa8 | Boise Air Terminal Uo | 5279470 | 73958.8 | 71.384 | 371.25 | 641.25 | 0.25 | 107 | 3447030 | 1832440 | 0 | 0 | 0 | 377.009 | 1151540 | 175763 | 1591590 | 0 | 166920 | 43940.8 | 1320360 | 373051 | 456270 | 28.4345 | 0 | 0 | 0 | 0 |  | 337483 | 51511.1 | 364308 | 0 | 594.444 | 12877.8 | 391.667 | 109331 | 133719 | 8.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 3485.89 | 0 | 1649.24 | 0 | 13192.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1151540 | 1220250 | 104557 | 703572 | 190611 | 9669.72 | 130893 | 394087 | 1013020 | 897265 | 187031 | 369812 | 1144010 | 529653 | 533374 | 1360400
| bonus - 0 ot 2 error as single step | [15 empty] | 0 | 95369.2 | 0 | 0 | 40718 | 28.4 | 709720 | 90109 | 88725 | 3345.7955 | 0 | 0 | 369.7 | 0 | 17.73%
PrimarySchool | 0 - Prototype¦1 - Prototype-NewHvac |  | Boise Air Terminal Uo | 1066650 | 0 | 14.4221 | 55.75 | 1795 | 4 | 318.75 | 155900 | 910750 | 0 | 0 | 0 | 32.253 | 0% | 0% | 0% | 0% | 0.0001552% | 0.001473% | 15.7% | 0.8913% | 1.753% | 0.05671% | 0% | 0% | 0.004085% | 0% | 18.4% | 0 | 0 | 0 | 0 | 0 | 25 | 125 | 15150 | 29795 | 963.889 | 0 | 0 | 69.44 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 9109.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9061 | 43704 | 1650.68 | 23120 | 4296 | 16540 | 10579 | 5322 | 113790 | 189712 | 5862 | 15079 | 20070
PrimarySchool | 1 - Prototype-NewHvac¦2 - Prototype-NewHvacLoadsConstSch |  | Boise Air Terminal Uo | 310440 | 0 | 4.1974 | 251.5 | 483.5 | 0.75 | 2.25 | 71110 | 239340 | 0 | 0 | 0 | 6.879 | 0% | 2.015% | 0% | 0% | 0.8601% | 0.002404% | 4.239% | 0.8117% | 0.2734% | 0.001202% | 0% | 0% | 0.01282% | 0% | 8.215% | 0 | 27950 | 0 | 0 | 0 | 33.3 | 583.333 | 11258 | 3792 | 16.6667 | 0 | 0 | 177.78 | 0 | 0 | 0 | 0 | 0 | 407.17 | 0 | 1986.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4966 | 1749 | 6033.9 | 30249 | 2535 | 9270 | 9256 | 50347 | 101626 | 232222 | 7603 | 21619 | 26020
PrimarySchool | 2 - Prototype-NewHvacLoadsConstSch¦3b - Typical-Bar-Sliced |  | Boise Air Terminal Uo | 413980 | 30.2 | 5.5674 | 1392 | 185.5 | 1.25 | 39.5 | 303250 | 110720 | 0 | 0 | 0 | 15.577 | 0.008923% | 0.005631% | 0.008129% | 0% | 0.5405% | 0.9194% | 2.734% | 1.184% | 5.406% | 0% | 0% | 0% | 0.3492% | 0% | 11.16% | 131 | 83.3 | 48 | 0 | 594.444 | 13588.9 | 397.227 | 17500 | 79908 | 0 | 0 | 0 | 5161.07 | 0 | 0 | 0 | 5.78 | 0 | 252.36 | 0 | 1365.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 190 | 174 | 18707 | 12353 | 165.01 | 140435 | 39209 | 109528 | 1487 | 14729 | 176872 | 123490 | 41587 | 65548 | 56510
PrimarySchool | 2 - Prototype-NewHvacLoadsConstSch¦4b - Typical-Bar-Blend |  | Boise Air Terminal Uo | 118460 | 30.2 | 1.5733 | 120.25 | 1538 | 1.75 | 62.75 | 233760 | 115310 | 0 | 0 | 0 | 6.029 | 0.008923% | 0.005631% | 0.008129% | 0% | 0.5407% | 0.9194% | 1.799% | 0.03684% | 4.608% | 0% | 0% | 0% | 1.042% | 0% | 8.968% | 131 | 83.3 | 48 | 0 | 594.444 | 13588.9 | 358.333 | 545 | 68108 | 0 | 0 | 0 | 15394.47 | 0 | 0 | 0 | 5.78 | 0 | 252.46 | 0 | 895.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 190 | 174 | 11888 | 40579 | 62.98 | 144050 | 40694 | 111712 | 856 | 7912 | 162845 | 109600 | 41826 | 66844 | 62360
PrimarySchool | 2 - Prototype-NewHvacLoadsConstSch¦4c - Typical-Urban-Blend |  | Boise Air Terminal Uo | 67240 | 4.8 | 0.9047 | 612.75 | 1908.5 | 1.25 | 13.5 | 138280 | 205500 | 0 | 0 | 0 | 58.897 | 0.0009914% | 0.005631% | 0.01923% | 0% | 0.5407% | 0.9194% | 4.551% | 2.176% | 1.013% | 0% | 0% | 0% | 0.5706% | 0% | 9.796% | 14 | 83.3 | 80 | 0 | 594.444 | 13588.9 | 566.666 | 32161.2 | 14969 | 0 | 0 | 0 | 8433.33 | 0 | 0 | 0 | 7.01 | 0 | 252.46 | 0 | 2314.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 230 | 209 | 665 | 21290 | 62.07 | 178813 | 1758 | 230724 | 10325 | 9152 | 6681 | 154890 | 10085 | 127129 | 71560
PrimarySchool | 2 - Prototype-NewHvacLoadsConstSch¦4d - Prototype-Prototype-Blend |  | Boise Air Terminal Uo | 236100 | 0 | 3.1924 | 393.75 | 1426.75 | 1 | 81.5 | 67100 | 303190 | 0 | 0 | 0 | 2.574 | 0% | 0% | 0% | 0% | 0% | 0.04811% | 5.99% | 0.07838% | 0.6119% | 0% | 0% | 0% | 0.5706% | 0% | 7.299% | 0 | 0 | 0 | 0 | 0 | 711.1 | 316.666 | 1158 | 9045 | 0 | 0 | 0 | 8433.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3032.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4833 | 15613 | 45.16 | 3532 | 797 | 1400 | 913 | 1054 | 43336 | 7730 | 2692 | 5022 | 3630
chart | [19 empty] | look at heating drop from 0 to 1
FullServiceRestaurant | 0 - Prototype | run/Prototype Row B/datapoint_59c942e553ff6b03c8620176 | Boise Air Terminal Uo | 2713550 | 5501.97 | 493.196 | 23.5 | 149.5 | 0 | 0.5 | 1181620 | 1531930 | 0 | 0 | 0 | 87.4723 | 176995 | 54945 | 881915 | 0 | 253977 | 34140.4 | 834733 | 64859.1 | 411741 | 246.432 | 0 | 0 | 0 | 0 |  | 51872.2 | 16102.8 | 127972 | 0 | 594.444 | 10005.6 | 0 | 19008.3 | 120669 | 72.2222 | 0 | 0 | 0 | 0 | 0 | 0 | 4453.42 | 0 | 2519.97 | 0 | 8348.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176999 | 381251 | 133576 | 226246 | 43844.6 | 7675.5 | 590.7 | 55248.3 | 71742.7 | 67827.4 | 161332 | 186073 | 84296.3 | 78125.9 | 30554.1 | 83676.6
FullServiceRestaurant | 1 - Prototype-NewHvac | run/Prototype Row B/datapoint_59c942ed53ff6b03c8620186 | Boise Air Terminal Uo | 2676830 | 5501.97 | 486.523 | 113.25 | 247 | 72.5 | 75.5 | 1275550 | 1401280 | 0 | 0 | 0 | 94.3773 | 176995 | 54945 | 881915 | 0 | 253977 | 34301.5 | 704086 | 72849.2 | 497509 | 246.432 | 0 | 0 | 0 | 0 |  | 51872.2 | 16102.8 | 127972 | 0 | 594.444 | 10052.8 | 0 | 21350 | 145806 | 72.2222 | 0 | 0 | 0 | 0 | 0 | 0 | 4453.42 | 0 | 2519.97 | 0 | 7042.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176999 | 381251 | 133576 | 224319 | 46562.5 | 7653.29 | 117.3 | 55066.6 | 71470.4 | 67548.9 | 164478 | 142797 | 95808.6 | 78999.4 | 31432.2 | 84171.6
FullServiceRestaurant | 2 - Prototype-NewHvacLoadsConstSch | run/Prototype Row B/datapoint_59c942f553ff6b03c8620196 | Boise Air Terminal Uo | 1866800 | 5501.97 | 339.297 | 35 | 324.5 | 5.5 | 105.25 | 1023520 | 843282 | 0 | 0 | 0 | 70.2357 | 176995 | 58196 | 841036 | 0 | 270498 | 34965 | 129567 | 58262.3 | 251721 | 0 | 0 | 0 | 45561.6 | 0 |  | 51872.2 | 17055.6 | 115992 | 0 | 594.444 | 10247.2 | 0 | 17075 | 73772.2 | 0 | 0 | 0 | 13352.8 | 0 | 0 | 0 | 4453.42 | 0 | 2685.21 | 0 | 1295.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176999 | 340373 | 133576 | 219701 | 15447.5 | 980.927 | 35.4 | 54215 | 70915.8 | 65053.5 | 20397.2 | 6455.74 | 151220 | 81124.1 | 32724.4 | 90483.2
FullServiceRestaurant | 3b - Typical-Bar-Sliced | run/Prototype Row B/datapoint_59c9430753ff6b03c86201a6 | Boise Air Terminal Uo | 2168520 | 5500.04 | 394.274 | 178.5 | 130.75 | 107.5 | 102 | 894900 | 1273620 | 0 | 0 | 0 | 70.8045 | 176929 | 58177 | 840903 | 0 | 245257 | 0 | 583173 | 85246.7 | 178834 | 0 | 0 | 0 | 0 | 0 |  | 51852.8 | 17050 | 115967 | 0 | 0 | 0 | 5.5556 | 24983.3 | 52411.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4452.95 | 0 | 2453.04 | 0 | 5832.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176928 | 340296 | 133563 | 223779 | 31037.1 | 981.087 | 3982.6 | 54120.5 | 59928.3 | 56735.8 | 19258.4 | 98896.6 | 177604 | 80398.9 | 30965.7 | 82718.5
FullServiceRestaurant | 4b - Typical-Bar-Blend | run/Prototype Row B/datapoint_59c9431053ff6b03c86201b6 | Boise Air Terminal Uo | 2073400 | 5500.04 | 376.979 | 188.75 | 204 | 86.25 | 149.5 | 888635 | 1184760 | 0 | 0 | 0 | 69.0732 | 176929 | 58177 | 840903 | 0 | 245257 | 0 | 494306 | 79863.1 | 177962 | 0 | 0 | 0 | 0 | 0 |  | 51852.8 | 17050 | 115967 | 0 | 0 | 0 | 2.7778 | 23405.6 | 52155.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4452.95 | 0 | 2453.04 | 0 | 4943.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176928 | 340296 | 133563 | 222138 | 24972.8 | 1127.94 | 2010.7 | 54459.9 | 60538.6 | 56735.5 | 18979.4 | 84026.4 | 174534 | 79814.1 | 31121.4 | 82663.1
FullServiceRestaurant | 4c - Typical-Urban-Blend | run/Prototype Row B/datapoint_59c9432b53ff6b03c86201c8 | Boise Air Terminal Uo | 2090890 | 5502.3 | 380.004 | 146.75 | 77.5 | 43 | 64 | 922672 | 1168220 | 0 | 0 | 0 | 71.3388 | 177005 | 58177 | 841254 | 0 | 245248 | 0 | 477605 | 85872.2 | 205733 | 0 | 0 | 0 | 0 | 0 |  | 51875 | 17050 | 116017 | 0 | 0 | 0 | 8.3333 | 25166.7 | 60294.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4454.75 | 0 | 2452.95 | 0 | 4776.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177001 | 340437 | 133618 | 221762 | 25629.2 | 1128.77 | 4608.5 | 45239.6 | 100502 | 55521.8 | 18836.5 | 86161.7 | 206358 | 69072.2 | 48817.1 | 83176.9
FullServiceRestaurant | 4d - Prototype-Prototype-Blend | run/Prototype Row B/datapoint_59c991be45b421004abe3aa9 | Boise Air Terminal Uo | 2068420 | 5501.97 | 375.942 | 39.25 | 323.75 | 5 | 105.5 | 999994 | 1068430 | 0 | 0 | 0 | 75.4189 | 176995 | 58196 | 841036 | 0 | 270498 | 34462.6 | 354702 | 80308.5 | 252214 | 0 | 0 | 0 | 0 | 0 |  | 51872.2 | 17055.6 | 115992 | 0 | 594.444 | 10100 | 0 | 23536.1 | 73916.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4453.42 | 0 | 2685.21 | 0 | 3547.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176999 | 340373 | 133576 | 220808 | 25680.7 | 1127.88 | 38.8 | 54914.4 | 71012.6 | 65288.2 | 19774.6 | 9496.22 | 142081 | 79999.1 | 32808.9 | 90055.3
| bonus - 0 ot 2 error as single step | [15 empty] | 0 | 3251 | 40879 | 0 | 16521 | 824.6 | 705166 | 6596.8 | 160020 | 246.432 | 0 | 0 | 45561.6 | 0 | 36.08%
FullServiceRestaurant | 0 - Prototype¦1 - Prototype-NewHvac |  | Boise Air Terminal Uo | 36720 | 0 | 6.673 | 89.75 | 97.5 | 72.5 | 75 | 93930 | 130650 | 0 | 0 | 0 | 6.905 | 0% | 0% | 0% | 0% | 0% | 0.005937% | 4.815% | 0.2945% | 3.161% | 0% | 0% | 0% | 0% | 0% | 8.276% | 0 | 0 | 0 | 0 | 0 | 47.2 | 0 | 2341.7 | 25137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1306.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1927 | 2717.9 | 22.21 | 473.4 | 181.7 | 272.3 | 278.5 | 3146 | 43276 | 11512.3 | 873.5 | 878.1 | 495
FullServiceRestaurant | 1 - Prototype-NewHvac¦2 - Prototype-NewHvacLoadsConstSch |  | Boise Air Terminal Uo | 810030 | 0 | 147.226 | 78.25 | 77.5 | 67 | 29.75 | 252030 | 557998 | 0 | 0 | 0 | 24.1416 | 0% | 0.1214% | 1.527% | 0% | 0.6172% | 0.02479% | 21.46% | 0.5449% | 9.182% | 0.009206% | 0% | 0% | 1.702% | 0% | 35.19% | 0 | 952.8 | 11980 | 0 | 0 | 194.4 | 0 | 4275 | 72033.8 | 72.2222 | 0 | 0 | 13352.8 | 0 | 0 | 0 | 0 | 0 | 165.24 | 0 | 5746.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40878 | 0 | 4618 | 31115 | 6672.363 | 81.9 | 851.6 | 554.6 | 2495.4 | 144080.8 | 136341.26 | 55411.4 | 2124.7 | 1292.2 | 6311.6
FullServiceRestaurant | 2 - Prototype-NewHvacLoadsConstSch¦3b - Typical-Bar-Sliced |  | Boise Air Terminal Uo | 301720 | 1.93 | 54.977 | 143.5 | 193.75 | 102 | 3.25 | 128620 | 430338 | 0 | 0 | 0 | 0.5688 | 0.003535% | 0.001018% | 0.007124% | 0% | 1.352% | 1.873% | 24.3% | 1.445% | 3.904% | 0% | 0% | 0% | 2.441% | 0% | 35.33% | 19.4 | 5.6 | 25 | 0 | 594.444 | 10247.2 | 5.5556 | 7908.3 | 21361.1 | 0 | 0 | 0 | 13352.8 | 0 | 0 | 0 | 0.47 | 0 | 232.17 | 0 | 4536.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 77 | 13 | 4078 | 15589.6 | 0.16 | 3947.2 | 94.5 | 10987.5 | 8317.7 | 1138.8 | 92440.86 | 26384 | 725.2 | 1758.7 | 7764.7
FullServiceRestaurant | 2 - Prototype-NewHvacLoadsConstSch¦4b - Typical-Bar-Blend |  | Boise Air Terminal Uo | 206600 | 1.93 | 37.682 | 153.75 | 120.5 | 80.75 | 44.25 | 134885 | 341478 | 0 | 0 | 0 | 1.1625 | 0.003535% | 0.001018% | 0.007124% | 0% | 1.352% | 1.873% | 19.54% | 1.157% | 3.951% | 0% | 0% | 0% | 2.441% | 0% | 30.32% | 19.4 | 5.6 | 25 | 0 | 594.444 | 10247.2 | 2.7778 | 6330.6 | 21616.6 | 0 | 0 | 0 | 13352.8 | 0 | 0 | 0 | 0.47 | 0 | 232.17 | 0 | 3647.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 77 | 13 | 2437 | 9525.3 | 147.013 | 1975.3 | 244.9 | 10377.2 | 8318 | 1417.8 | 77570.66 | 23314 | 1310 | 1603 | 7820.1
FullServiceRestaurant | 2 - Prototype-NewHvacLoadsConstSch¦4c - Typical-Urban-Blend |  | Boise Air Terminal Uo | 224090 | 0.33 | 40.707 | 111.75 | 247 | 37.5 | 41.25 | 100848 | 324938 | 0 | 0 | 0 | 1.1031 | 0.0005357% | 0.001018% | 0.01168% | 0% | 1.353% | 1.873% | 18.64% | 1.479% | 2.463% | 0% | 0% | 0% | 2.441% | 0% | 28.27% | 2.8 | 5.6 | 25 | 0 | 594.444 | 10247.2 | 8.3333 | 8091.7 | 13477.8 | 0 | 0 | 0 | 13352.8 | 0 | 0 | 0 | 1.33 | 0 | 232.26 | 0 | 3480.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 64 | 42 | 2061 | 10181.7 | 147.843 | 4573.1 | 8975.4 | 29586.2 | 9531.7 | 1560.7 | 79705.96 | 55138 | 12051.9 | 16092.7 | 7306.3
FullServiceRestaurant | 2 - Prototype-NewHvacLoadsConstSch¦4d - Prototype-Prototype-Blend |  | Boise Air Terminal Uo | 201620 | 0 | 36.645 | 4.25 | 0.75 | 0.5 | 0.25 | 23526 | 225148 | 0 | 0 | 0 | 5.1832 | 0% | 0% | 0% | 0% | 0% | 0.02691% | 12.06% | 1.181% | 0.02641% | 0% | 0% | 0% | 2.441% | 0% | 15.73% | 0 | 0 | 0 | 0 | 0 | 147.2 | 0 | 6461.1 | 144.5 | 0 | 0 | 0 | 13352.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2251.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1107 | 10233.2 | 146.953 | 3.4 | 699.4 | 96.8 | 234.7 | 622.6 | 3040.48 | 9139 | 1125 | 84.5 | 427.9
chart | [19 empty] | loss of infiltration and ventilation from 1 to 2
QuickServiceRestaurant | 0 - Prototype | run/Prototype Row B/datapoint_59c942e553ff6b03c862017c | Boise Air Terminal Uo | 1455590 | 2500.89 | 582.03 | 190.5 | 172.75 | 0 | 0 | 597807 | 857774 | 0 | 0 | 0 | 42.8026 | 71579.1 | 25922.8 | 714692 | 0 | 67873.2 | 35249.3 | 337641 | 28406.1 | 174228 | 0 | 0 | 0 | 0 | 0 |  | 20977.8 | 7597.22 | 76911.1 | 0 | 0 | 10330.6 | 0 | 8325 | 51061.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4523.48 | 0 | 678.863 | 0 | 3377.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71580.5 | 215990 | 135679 | 74124 | 15709 | 9770.98 | 186 | 38384.9 | 40156.6 | 30086.8 | 145640 | 179314 | 44995.4 | 55547 | 16762.2 | 38156.8
QuickServiceRestaurant | 1 - Prototype-NewHvac | run/Prototype Row B/datapoint_59c942ed53ff6b03c862018c | Boise Air Terminal Uo | 1470490 | 2500.89 | 587.988 | 266 | 266 | 106.75 | 64 | 629351 | 841140 | 0 | 0 | 0 | 46.2138 | 71579.1 | 25922.8 | 714692 | 0 | 67873.2 | 35467.3 | 320997 | 33780.2 | 200179 | 0 | 0 | 0 | 0 | 0 |  | 20977.8 | 7597.22 | 76911.1 | 0 | 0 | 10394.4 | 0 | 9900 | 58666.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4523.48 | 0 | 678.863 | 0 | 3210.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71580.5 | 215990 | 135679 | 73320.3 | 17592.7 | 9759.24 | 48.6 | 38170.5 | 39982.1 | 29911.6 | 148423 | 183058 | 52114.5 | 56358.2 | 17256.3 | 38481
QuickServiceRestaurant | 2 - Prototype-NewHvacLoadsConstSch | run/Prototype Row B/datapoint_59c942f553ff6b03c862019c | Boise Air Terminal Uo | 1141170 | 2500.89 | 456.307 | 144 | 210.5 | 21.25 | 85.5 | 472752 | 668420 | 0 | 0 | 0 | 33.1313 | 71579.1 | 33704.4 | 673813 | 0 | 73455.8 | 35742.2 | 142703 | 25164.5 | 85009.7 | 0 | 0 | 0 | 0 | 0 |  | 20977.8 | 9877.78 | 64930.6 | 0 | 0 | 10475 | 0 | 7375 | 24913.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4523.48 | 0 | 734.7 | 0 | 1427.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71580.5 | 175112 | 135679 | 72278.4 | 10059.4 | 634.169 | 16.6 | 37864 | 39777.1 | 29133 | 13380.8 | 20328.7 | 66538.4 | 57043.3 | 17647.9 | 40515.7
QuickServiceRestaurant | 3b - Typical-Bar-Sliced | run/Prototype Row B/datapoint_59c9430753ff6b03c86201ac | Boise Air Terminal Uo | 1273250 | 2497.01 | 509.91 | 6.5 | 48.25 | 0 | 48.25 | 482031 | 791219 | 0 | 0 | 0 | 36.0602 | 71465.4 | 33647.5 | 672761 | 0 | 63010.9 | 0 | 276696 | 45163.5 | 110497 | 0 | 0 | 0 | 0 | 0 |  | 20944.4 | 9861.11 | 64830.6 | 0 | 0 | 0 | 11.1111 | 13236.1 | 32383.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4516.37 | 0 | 630.23 | 0 | 2767.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71468.3 | 174838 | 135466 | 72293.3 | 10667.5 | 633.461 | 3517.1 | 35914 | 40228.7 | 25867.9 | 12666.5 | 69662.4 | 76134.3 | 53723.9 | 20394.8 | 37257.3
QuickServiceRestaurant | 4b - Typical-Bar-Blend | run/Prototype Row B/datapoint_59c9431053ff6b03c86201bc | Boise Air Terminal Uo | 1256050 | 2497.01 | 503.02 | 303.75 | 141.25 | 84.25 | 110.25 | 484761 | 771277 | 0 | 0 | 0 | 37.0241 | 71465.4 | 33647.5 | 672761 | 0 | 63010.9 | 0 | 256802 | 49589.8 | 108762 | 0 | 0 | 0 | 0 | 0 |  | 20944.4 | 9861.11 | 64830.6 | 0 | 0 | 0 | 25 | 14533.3 | 31875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4516.37 | 0 | 630.23 | 0 | 2567.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71468.3 | 174838 | 135466 | 71961.4 | 9117.02 | 776.067 | 1653.1 | 36211.4 | 40799.8 | 25662.3 | 12773.3 | 66171.7 | 79291.1 | 54615.3 | 20861.4 | 37423.6
QuickServiceRestaurant | 4c - Typical-Urban-Blend | run/Prototype Row B/datapoint_59c9432b53ff6b03c86201ce | Boise Air Terminal Uo | 1158440 | 2500.99 | 463.192 | 377.25 | 75 | 73.75 | 62 | 434205 | 724237 | 0 | 0 | 0 | 32.892 | 71579.1 | 33647.5 | 673851 | 0 | 63010.9 | 0 | 208994 | 42206.3 | 65134 | 0 | 0 | 0 | 0 | 0 |  | 20977.8 | 9861.11 | 64933.3 | 0 | 0 | 0 | 16.6667 | 12369.4 | 19088.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4523.76 | 0 | 630.23 | 0 | 2089.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71583.9 | 175120 | 135685 | 71951.2 | 6348.77 | 777.671 | 2540.6 | 29772.4 | 67313.1 | 24948 | 12827 | 72468 | 100419 | 47278.8 | 32562.1 | 37958.5
QuickServiceRestaurant | 4d - Prototype-Prototype-Blend | run/Prototype Row B/datapoint_59c991be45b421004abe3aaf | Boise Air Terminal Uo | 1165620 | 2500.89 | 466.081 | 175.5 | 377.25 | 24 | 118.25 | 495614 | 670012 | 0 | 0 | 0 | 34.8796 | 71579.1 | 33704.4 | 673813 | 0 | 73455.8 | 35533.7 | 144296 | 35164 | 98080.1 | 0 | 0 | 0 | 0 | 0 |  | 20977.8 | 9877.78 | 64930.6 | 0 | 0 | 10413.9 | 0 | 10305.6 | 28744.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4523.48 | 0 | 734.7 | 0 | 1443.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71580.5 | 175112 | 135679 | 71749 | 6485.96 | 776.66 | 18.1 | 38166.5 | 39711.5 | 29189.2 | 13402 | 18002.4 | 65703.8 | 56931.6 | 18148.9 | 40493.3
| bonus - 0 ot 2 error as single step | [15 empty] | 0 | 7781.6 | 40879 | 0 | 5582.6 | 492.9 | 194938 | 3241.6 | 89218.3 | 0 | 0 | 0 | 0 | 0 | 23.5%
QuickServiceRestaurant | 0 - Prototype¦1 - Prototype-NewHvac |  | Boise Air Terminal Uo | 14900 | 0 | 5.958 | 75.5 | 93.25 | 106.75 | 64 | 31544 | 16634 | 0 | 0 | 0 | 3.4112 | 0% | 0% | 0% | 0% | 0% | 0.01498% | 1.143% | 0.3692% | 1.783% | 0% | 0% | 0% | 0% | 0% | 3.31% | 0 | 0 | 0 | 0 | 0 | 63.8 | 0 | 1575 | 7605.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 803.7 | 1883.7 | 11.74 | 137.4 | 214.4 | 174.5 | 175.2 | 2783 | 3744 | 7119.1 | 811.2 | 494.1 | 324.2
QuickServiceRestaurant | 1 - Prototype-NewHvac¦2 - Prototype-NewHvacLoadsConstSch |  | Boise Air Terminal Uo | 329320 | 0 | 131.681 | 122 | 55.5 | 85.5 | 21.5 | 156599 | 172720 | 0 | 0 | 0 | 13.0825 | 0% | 0.5292% | 2.78% | 0% | 0.3796% | 0.01869% | 12.12% | 0.5859% | 7.832% | 0% | 0% | 0% | 0% | 0% | 24.25% | 0 | 2280.56 | 11980.5 | 0 | 0 | 80.6 | 0 | 2525 | 33752.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.837 | 0 | 1783.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40878 | 0 | 1041.9 | 7533.3 | 9125.071 | 32 | 306.5 | 205 | 778.6 | 135042.2 | 162729.3 | 14423.9 | 685.1 | 391.6 | 2034.7
QuickServiceRestaurant | 2 - Prototype-NewHvacLoadsConstSch¦3b - Typical-Bar-Sliced |  | Boise Air Terminal Uo | 132080 | 3.88 | 53.603 | 137.5 | 162.25 | 21.25 | 37.25 | 9279 | 122799 | 0 | 0 | 0 | 2.9289 | 0.009963% | 0.004986% | 0.09219% | 0% | 0.9153% | 3.132% | 11.74% | 1.752% | 2.233% | 0% | 0% | 0% | 0% | 0% | 19.88% | 33.4 | 16.67 | 100 | 0 | 0 | 10475 | 11.1111 | 5861.1 | 7469.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.11 | 0 | 104.47 | 0 | 1339.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.2 | 274 | 213 | 14.9 | 608.1 | 0.708 | 3500.5 | 1950 | 451.6 | 3265.1 | 714.3 | 49333.7 | 9595.9 | 3319.4 | 2746.9 | 3258.4
QuickServiceRestaurant | 2 - Prototype-NewHvacLoadsConstSch¦4b - Typical-Bar-Blend |  | Boise Air Terminal Uo | 114880 | 3.88 | 46.713 | 159.75 | 69.25 | 63 | 24.75 | 12009 | 102857 | 0 | 0 | 0 | 3.8928 | 0.009963% | 0.004986% | 0.09219% | 0% | 0.9153% | 3.132% | 9.998% | 2.14% | 2.081% | 0% | 0% | 0% | 0% | 0% | 18.37% | 33.4 | 16.67 | 100 | 0 | 0 | 10475 | 25 | 7158.3 | 6961.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.11 | 0 | 104.47 | 0 | 1140.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.2 | 274 | 213 | 317 | 942.38 | 141.898 | 1636.5 | 1652.6 | 1022.7 | 3470.7 | 607.5 | 45843 | 12752.7 | 2428 | 3213.5 | 3092.1
QuickServiceRestaurant | 2 - Prototype-NewHvacLoadsConstSch¦4c - Typical-Urban-Blend |  | Boise Air Terminal Uo | 17270 | 0.1 | 6.885 | 233.25 | 135.5 | 52.5 | 23.5 | 38547 | 55817 | 0 | 0 | 0 | 0.2393 | 0% | 0.004986% | 0.00333% | 0% | 0.9153% | 3.132% | 5.809% | 1.493% | 1.742% | 0% | 0% | 0% | 0% | 0% | 13.1% | 0 | 16.67 | 2.7 | 0 | 0 | 10475 | 16.6667 | 4994.4 | 5825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28 | 0 | 104.47 | 0 | 662.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 8 | 6 | 327.2 | 3710.63 | 143.502 | 2524 | 8091.6 | 27536 | 4185 | 553.8 | 52139.3 | 33880.6 | 9764.5 | 14914.2 | 2557.2
QuickServiceRestaurant | 2 - Prototype-NewHvacLoadsConstSch¦4d - Prototype-Prototype-Blend |  | Boise Air Terminal Uo | 24450 | 0 | 9.774 | 31.5 | 166.75 | 2.75 | 32.75 | 22862 | 1592 | 0 | 0 | 0 | 1.7483 | 0% | 0% | 0% | 0% | 0% | 0.01827% | 0.1396% | 0.8762% | 1.145% | 0% | 0% | 0% | 0% | 0% | 2.179% | 0 | 0 | 0 | 0 | 0 | 61.1 | 0 | 2930.6 | 3830.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 529.4 | 3573.44 | 142.491 | 1.5 | 302.5 | 65.6 | 56.2 | 21.2 | 2326.3 | 834.6 | 111.7 | 501 | 22.4
chart | [19 empty] | loss of infiltration and ventilation from 1 to 2
SmallOffice | 0 - Prototype | run/Prototype Row B/datapoint_59c942e553ff6b03c8620182 | Boise Air Terminal Uo | 219666 | 5502.08 | 39.9242 | 231.5 | 100.75 | 28.5 | 17 | 216083 | 3582.75 | 0 | 0 | 0 | 21.4224 | 68460.8 | 24302 | 50983.1 | 0 | 17070.2 | 0 | 17136.5 | 16729 | 24993.9 | 0 | 0 | 0 | 0 | 0 |  | 20063.9 | 7122.22 | 14941.7 | 0 | 5002.78 | 0 | 3972.22 | 4902.78 | 7325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.8344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68456.7 | 50981.2 | 0 | 19862.6 | 1266.69 | 285.176 | 12020.1 | 75970.1 | 59739.8 | 83889.9 | 13382.2 | 18744.4 | 75813.6 | 103590 | 34652.1 | 112727
SmallOffice | 1 - Prototype-NewHvac | run/Prototype Row B/datapoint_59c942ed53ff6b03c8620192 | Boise Air Terminal Uo | 289198 | 5502.08 | 52.5616 | 21.75 | 11.5 | 21.75 | 11.5 | 239864 | 49333.9 | 0 | 0 | 0 | 20.9222 | 68460.8 | 24302 | 50983.1 | 0 | 17070.2 | 0 | 49637.2 | 16681.6 | 62072.5 | 0 | 0 | 0 | 0 | 0 |  | 20063.9 | 7122.22 | 14941.7 | 0 | 5002.78 | 0 | 88.8889 | 4888.89 | 18191.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 493.434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68456.7 | 50981.2 | 0 | 19937.7 | 1450.73 | 265.365 | 17172.5 | 76138.8 | 59899.2 | 84213.1 | 13095.1 | 23925 | 71708.4 | 103011 | 34000.6 | 111903
SmallOffice | 2 - Prototype-NewHvacLoadsConstSch | run/Prototype Row B/datapoint_59c942f553ff6b03c86201a2 | Boise Air Terminal Uo | 300145 | 5502.08 | 54.5512 | 23 | 9 | 23 | 9 | 242215 | 57940.1 | 0 | 0 | 0 | 20.7061 | 68460.8 | 29780.4 | 50983.1 | 0 | 20833 | 0 | 54490 | 14956.6 | 60650.8 | 0 | 0 | 0 | 0 | 0 |  | 20063.9 | 8727.78 | 14941.7 | 0 | 5002.78 | 0 | 91.6667 | 4383.33 | 17775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.6356 | 0 | 541.877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68456.7 | 50981.2 | 0 | 20030.5 | 1516.82 | 864.837 | 17336.2 | 76431.2 | 60230.1 | 84537.4 | 18661 | 25126.4 | 79078.3 | 102487 | 33522.4 | 111271
SmallOffice | 3b - Typical-Bar-Sliced | run/Prototype Row B/datapoint_59c9430753ff6b03c86201b2 | Boise Air Terminal Uo | 289757 | 5500.04 | 52.6828 | 31.25 | 0.25 | 31.25 | 0.25 | 239210 | 50547.1 | 0 | 0 | 0 | 21.2469 | 68432.4 | 29761.5 | 50964.1 | 0 | 3753.36 | 0 | 47239.2 | 21126.8 | 68479.8 | 0 | 0 | 0 | 0 | 0 |  | 20055.6 | 8722.22 | 14936.1 | 0 | 0 | 0 | 130.556 | 6191.67 | 20069.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.5408 | 0 | 468.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68431.2 | 50962.2 | 0 | 19580.5 | 1724.68 | 819.762 | 31096.6 | 96607.5 | 49898.5 | 69855.6 | 18024.5 | 23515.1 | 82318.1 | 119406 | 24038 | 96272.1
SmallOffice | 4b - Typical-Bar-Blend | run/Prototype Row B/datapoint_59c9431053ff6b03c86201c2 | Boise Air Terminal Uo | 289596 | 5500.04 | 52.6535 | 31.25 | 0.25 | 31.25 | 0.25 | 239987 | 49608.7 | 0 | 0 | 0 | 21.1801 | 68432.4 | 29761.5 | 50964.1 | 0 | 3753.36 | 0 | 46310.3 | 21136.3 | 69238 | 0 | 0 | 0 | 0 | 0 |  | 20055.6 | 8722.22 | 14936.1 | 0 | 0 | 0 | 133.333 | 6194.44 | 20291.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.5408 | 0 | 458.642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68431.2 | 50962.2 | 0 | 19598.7 | 1757.07 | 825.293 | 31830.6 | 96526.4 | 49840.9 | 69750.8 | 17989.7 | 24410.7 | 83031.1 | 119416 | 24001.5 | 96177
SmallOffice | 4c - Typical-Urban-Blend | run/Prototype Row B/datapoint_59c9432b53ff6b03c86201d4 | Boise Air Terminal Uo | 242565 | 5501.97 | 44.087 | 572 | 78.5 | 107.75 | 15 | 199497 | 43068.8 | 0 | 0 | 0 | 19.8901 | 68451.4 | 29761.5 | 50983.1 | 0 | 3753.36 | 0 | 39571.4 | 19894.7 | 30140.6 | 0 | 0 | 0 | 0 | 0 |  | 20061.1 | 8722.22 | 14941.7 | 0 | 0 | 0 | 75 | 5830.56 | 8833.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.5408 | 0 | 393.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68455.5 | 50980.2 | 0 | 19499.9 | 1700.41 | 833.117 | 38043.6 | 78479.6 | 97227.3 | 67072.8 | 17834.7 | 22255.3 | 102493 | 97852.1 | 44235.1 | 94736.1
SmallOffice | 4d - Prototype-Prototype-Blend | run/Prototype Row B/datapoint_59c991be45b421004abe3ab5 | Boise Air Terminal Uo | 299188 | 5502.08 | 54.3772 | 23 | 9 | 23 | 9 | 241665 | 57523 | 0 | 0 | 0 | 20.6375 | 68460.8 | 29780.4 | 50983.1 | 0 | 20833 | 0 | 54082.4 | 14842.8 | 60214.8 | 0 | 0 | 0 | 0 | 0 |  | 20063.9 | 8727.78 | 14941.7 | 0 | 5002.78 | 0 | 91.6667 | 4350 | 17647.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.6356 | 0 | 537.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68456.7 | 50981.2 | 0 | 20031.3 | 1513.95 | 865.863 | 17720.1 | 76480.7 | 60298.8 | 84580.2 | 18660.2 | 24970.1 | 79246.1 | 102464 | 33507.5 | 111208
| bonus - 0 ot 2 error as single step | [15 empty] | 0 | 5478.4 | 0 | 0 | 3762.8 | 0 | 37353.5 | 1772.4 | 35656.9 | 0 | 0 | 0 | 0 | 0 | 38.25%
SmallOffice | 0 - Prototype¦1 - Prototype-NewHvac |  | Boise Air Terminal Uo | 69532 | 0 | 12.6374 | 209.75 | 89.25 | 6.75 | 5.5 | 23781 | 45751.15 | 0 | 0 | 0 | 0.5002 | 0% | 0% | 0% | 0% | 0% | 0% | 14.8% | 0.02158% | 16.88% | 0% | 0% | 0% | 0% | 0% | 31.7% | 0 | 0 | 0 | 0 | 0 | 0 | 3883.3311 | 13.89 | 10866.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 457.5996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.1 | 184.04 | 19.811 | 5152.4 | 168.7 | 159.4 | 323.2 | 287.1 | 5180.6 | 4105.2 | 579 | 651.5 | 824
SmallOffice | 1 - Prototype-NewHvac¦2 - Prototype-NewHvacLoadsConstSch |  | Boise Air Terminal Uo | 10947 | 0 | 1.9896 | 1.25 | 2.5 | 1.25 | 2.5 | 2351 | 8606.2 | 0 | 0 | 0 | 0.2161 | 0% | 1.894% | 0% | 0% | 1.301% | 0% | 1.678% | 0.5965% | 0.4916% | 0% | 0% | 0% | 0% | 0% | 5.962% | 0 | 1605.56 | 0 | 0 | 0 | 0 | 2.7778 | 505.56 | 416.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.6356 | 0 | 48.443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.8 | 66.09 | 599.472 | 163.7 | 292.4 | 330.9 | 324.3 | 5565.9 | 1201.4 | 7369.9 | 524 | 478.2 | 632
SmallOffice | 2 - Prototype-NewHvacLoadsConstSch¦3b - Typical-Bar-Sliced |  | Boise Air Terminal Uo | 10388 | 2.04 | 1.8684 | 8.25 | 8.75 | 8.25 | 8.75 | 3005 | 7393 | 0 | 0 | 0 | 0.5408 | 0.009462% | 0.006297% | 0.00633% | 0% | 5.69% | 0% | 2.416% | 2.056% | 2.608% | 0% | 0% | 0% | 0% | 0% | 12.79% | 8.3 | 5.56 | 5.6 | 0 | 5002.78 | 0 | 38.8893 | 1808.34 | 2294.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0948 | 0 | 73.849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5 | 19 | 0 | 450 | 207.86 | 45.075 | 13760.4 | 20176.3 | 10331.6 | 14681.8 | 636.5 | 1611.3 | 3239.8 | 16919 | 9484.4 | 14998.9
SmallOffice | 2 - Prototype-NewHvacLoadsConstSch¦4b - Typical-Bar-Blend |  | Boise Air Terminal Uo | 10549 | 2.04 | 1.8977 | 8.25 | 8.75 | 8.25 | 8.75 | 2228 | 8331.4 | 0 | 0 | 0 | 0.474 | 0.009462% | 0.006297% | 0.00633% | 0% | 5.69% | 0% | 2.725% | 2.059% | 2.861% | 0% | 0% | 0% | 0% | 0% | 13.36% | 8.3 | 5.56 | 5.6 | 0 | 5002.78 | 0 | 41.6663 | 1811.11 | 2516.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0948 | 0 | 83.235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5 | 19 | 0 | 431.8 | 240.25 | 39.544 | 14494.4 | 20095.2 | 10389.2 | 14786.6 | 671.3 | 715.7 | 3952.8 | 16929 | 9520.9 | 15094
SmallOffice | 2 - Prototype-NewHvacLoadsConstSch¦4c - Typical-Urban-Blend |  | Boise Air Terminal Uo | 57580 | 0.11 | 10.4642 | 549 | 69.5 | 84.75 | 6 | 42718 | 14871.3 | 0 | 0 | 0 | 0.816 | 0.003132% | 0.006297% | 0% | 0% | 5.69% | 0% | 4.97% | 1.645% | 10.17% | 0% | 0% | 0% | 0% | 0% | 22.48% | 2.8 | 5.56 | 0 | 0 | 5002.78 | 0 | 16.6667 | 1447.23 | 8941.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0948 | 0 | 148.647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 1 | 0 | 530.6 | 183.59 | 31.72 | 20707.4 | 2048.4 | 36997.2 | 17464.6 | 826.3 | 2871.1 | 23414.7 | 4634.9 | 10712.7 | 16534.9
SmallOffice | 2 - Prototype-NewHvacLoadsConstSch¦4d - Prototype-Prototype-Blend |  | Boise Air Terminal Uo | 957 | 0 | 0.174 | 0 | 0 | 0 | 0 | 550 | 417.1 | 0 | 0 | 0 | 0.0686 | 0% | 0% | 0% | 0% | 0% | 0% | 0.1358% | 0.03792% | 0.1453% | 0% | 0% | 0% | 0% | 0% | 0.319% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.33 | 127.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 2.87 | 1.026 | 383.9 | 49.5 | 68.7 | 42.8 | 0.8 | 156.3 | 167.8 | 23 | 14.9 | 63
chart | [19 empty] | look at heating and fan change in 0 to 1
MediumOffice | 0 - Prototype | run/Prototype Row B/datapoint_59c942e553ff6b03c862017a | Boise Air Terminal Uo | 2623240 | 53627.8 | 48.9155 | 149 | 233 | 29.75 | 142.25 | 2388050 | 235191 | 0 | 0 | 0 | 356.832 | 575894 | 213922 | 786584 | 0 | 55873.8 | 0 | 537972 | 263152 | 189800 | 47.3909 | 0 | 0 | 0 | 0 |  | 168778 | 62694.4 | 230525 | 0 | 0 | 0 | 105111 | 77122.2 | 55625 | 13.8889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 558.846 | 0 | 1793.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575892 | 624332 | 0 | 175749 | 40040.4 | 5706.62 | 11128.8 | 526173 | 752810 | 243045 | 149502 | 227414 | 199066 | 688225 | 427388 | 327896
MediumOffice | 1 - Prototype-NewHvac | run/Prototype Row B/datapoint_59c942ed53ff6b03c862018a | Boise Air Terminal Uo | 2489670 | 53627.8 | 46.4249 | 722.5 | 1649.75 | 516.5 | 1055 | 2267970 | 221685 | 0 | 0 | 0 | 218.265 | 575894 | 213922 | 786584 | 0 | 55854.9 | 0 | 166095 | 301643 | 389629 | 47.3909 | 0 | 0 | 0 | 0 |  | 168778 | 62694.4 | 230525 | 0 | 0 | 0 | 77.7778 | 88402.8 | 114189 | 13.8889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 558.656 | 0 | 1658.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575892 | 624332 | 0 | 168428 | 18785.5 | 3790.39 | 9122.4 | 518212 | 735399 | 237550 | 159834 | 86327.8 | 276143 | 701517 | 451845 | 334787
MediumOffice | 2 - Prototype-NewHvacLoadsConstSch | run/Prototype Row B/datapoint_59c942f553ff6b03c862019a | Boise Air Terminal Uo | 2499110 | 53627.8 | 46.601 | 780.25 | 1635.25 | 552.75 | 1042.5 | 2205750 | 293359 | 0 | 0 | 0 | 212.195 | 575894 | 239627 | 717564 | 0 | 84687.5 | 0 | 208946 | 284961 | 387392 | 47.3909 | 0 | 0 | 0 | 0 |  | 168778 | 70227.8 | 210297 | 0 | 0 | 0 | 80.5556 | 83513.9 | 113533 | 13.8889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 847.038 | 0 | 2087.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575892 | 620881 | 0 | 169457 | 19552.4 | 8716.3 | 6111 | 519413 | 738171 | 237737 | 213656 | 102726 | 334876 | 698745 | 445476 | 334254
MediumOffice | 3b - Typical-Bar-Sliced | run/Prototype Row B/datapoint_59c9430753ff6b03c86201aa | Boise Air Terminal Uo | 2592120 | 53626 | 48.337 | 1441.5 | 1631.25 | 719.5 | 1122.25 | 2276600 | 315509 | 0 | 0 | 0 | 216.378 | 575875 | 242973 | 717535 | 0 | 43343.7 | 0 | 274876 | 298799 | 438669 | 47.3909 | 0 | 0 | 0 | 0 |  | 168772 | 71208.3 | 210289 | 0 | 0 | 0 | 794.444 | 87569.4 | 128561 | 13.8889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 433.52 | 0 | 2722.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575873 | 620860 | 0 | 168684 | 20417.6 | 10882.2 | 12802.8 | 513151 | 727999 | 188289 | 206169 | 118680 | 389061 | 689381 | 421942 | 322305
MediumOffice | 4b - Typical-Bar-Blend | run/Prototype Row B/datapoint_59c9431053ff6b03c86201ba | Boise Air Terminal Uo | 2576290 | 53626 | 48.0418 | 1603 | 1566.5 | 781.75 | 1073.5 | 2266020 | 310268 | 0 | 0 | 0 | 215.229 | 575875 | 242973 | 717535 | 0 | 43343.7 | 0 | 269749 | 283502 | 443266 | 47.3909 | 0 | 0 | 0 | 0 |  | 168772 | 71208.3 | 210289 | 0 | 0 | 0 | 827.778 | 83086.1 | 129908 | 13.8889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 433.52 | 0 | 2669.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575873 | 620860 | 0 | 169085 | 20680.3 | 11957.8 | 12860.8 | 513105 | 727765 | 188705 | 228751 | 120904 | 387356 | 689343 | 421009 | 317444
MediumOffice | 4c - Typical-Urban-Blend | run/Prototype Row B/datapoint_59c9432b53ff6b03c86201cc | Boise Air Terminal Uo | 2600390 | 53626.8 | 48.4906 | 732.75 | 1049.25 | 426.25 | 666 | 2417010 | 183384 | 0 | 0 | 0 | 218.636 | 575884 | 242973 | 717545 | 0 | 43343.7 | 0 | 141964 | 300079 | 578557 | 47.3909 | 0 | 0 | 0 | 0 |  | 168775 | 71208.3 | 210292 | 0 | 0 | 0 | 563.889 | 87944.4 | 169558 | 13.8889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 433.52 | 0 | 1400.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575882 | 620869 | 0 | 167317 | 16307.9 | 11940.7 | 25118.4 | 531506 | 664161 | 187569 | 229975 | 47862.4 | 327076 | 729453 | 396649 | 311832
MediumOffice | 4d - Prototype-Prototype-Blend | run/Prototype Row B/datapoint_59c991be45b421004abe3aad | Boise Air Terminal Uo | 4200530 | 53627.8 | 78.3273 | 441 | 2586 | 338.25 | 1427 | 4048070 | 152456 | 0 | 0 | 0 | 337.652 | 1151790 | 239627 | 1435120 | 0 | 84678 | 0 | 67844.7 | 500334 | 721080 | 47.3909 | 0 | 0 | 0 | 0 |  | 337556 | 70227.8 | 420592 | 0 | 0 | 0 | 22.2222 | 146633 | 211328 | 13.8889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 846.943 | 0 | 677.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1151780 | 1241760 | 0 | 281701 | 20501.4 | 8405.75 | 2066.5 | 502386 | 723378 | 225122 | 578631 | 43191.4 | 449225 | 737409 | 489520 | 365977
| bonus - 0 ot 2 error as single step | [15 empty] | 0 | 25705 | 69020 | 0 | 28813.7 | 0 | 329026 | 21809 | 197592 | 0 | 0 | 0 | 0 | 0 | 25.62%
MediumOffice | 0 - Prototype¦1 - Prototype-NewHvac |  | Boise Air Terminal Uo | 133570 | 0 | 2.4906 | 573.5 | 1416.75 | 486.75 | 912.75 | 120080 | 13506 | 0 | 0 | 0 | 138.567 | 0% | 0% | 0% | 0% | 0.0007205% | 0% | 14.18% | 1.467% | 7.618% | 0% | 0% | 0% | 0% | 0% | 23.26% | 0 | 0 | 0 | 0 | 0 | 0 | 105033.2222 | 11280.6 | 58564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19 | 0 | 134.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7321 | 21254.9 | 1916.23 | 2006.4 | 7961 | 17411 | 5495 | 10332 | 141086.2 | 77077 | 13292 | 24457 | 6891
MediumOffice | 1 - Prototype-NewHvac¦2 - Prototype-NewHvacLoadsConstSch |  | Boise Air Terminal Uo | 9440 | 0 | 0.1761 | 57.75 | 14.5 | 36.25 | 12.5 | 62220 | 71674 | 0 | 0 | 0 | 6.07 | 0% | 1.032% | 2.772% | 0% | 1.158% | 0% | 1.721% | 0.67% | 0.08985% | 0% | 0% | 0% | 0% | 0% | 7.444% | 0 | 7533.4 | 20228 | 0 | 0 | 0 | 2.7778 | 4888.9 | 656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 288.382 | 0 | 428.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3451 | 0 | 1029 | 766.9 | 4925.91 | 3011.4 | 1201 | 2772 | 187 | 53822 | 16398.2 | 58733 | 2772 | 6369 | 533
MediumOffice | 2 - Prototype-NewHvacLoadsConstSch¦3b - Typical-Bar-Sliced |  | Boise Air Terminal Uo | 93010 | 1.8 | 1.736 | 661.25 | 4 | 166.75 | 79.75 | 70850 | 22150 | 0 | 0 | 0 | 4.183 | 0.0007603% | 0.1339% | 0.00116% | 0% | 1.654% | 0% | 2.638% | 0.5537% | 2.052% | 0% | 0% | 0% | 0% | 0% | 7.034% | 6 | 980.5 | 8 | 0 | 0 | 0 | 713.8884 | 4055.5 | 15028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413.518 | 0 | 635.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 21 | 0 | 773 | 865.2 | 2165.9 | 6691.8 | 6262 | 10172 | 49448 | 7487 | 15954 | 54185 | 9364 | 23534 | 11949
MediumOffice | 2 - Prototype-NewHvacLoadsConstSch¦4b - Typical-Bar-Blend |  | Boise Air Terminal Uo | 77180 | 1.8 | 1.4408 | 822.75 | 68.75 | 229 | 31 | 60270 | 16909 | 0 | 0 | 0 | 3.034 | 0.0007603% | 0.1339% | 0.00116% | 0% | 1.654% | 0% | 2.433% | 0.05838% | 2.236% | 0% | 0% | 0% | 0% | 0% | 6.517% | 6 | 980.5 | 8 | 0 | 0 | 0 | 747.2224 | 427.8 | 16375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413.518 | 0 | 582.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 21 | 0 | 372 | 1127.9 | 3241.5 | 6749.8 | 6308 | 10406 | 49032 | 15095 | 18178 | 52480 | 9402 | 24467 | 16810
MediumOffice | 2 - Prototype-NewHvacLoadsConstSch¦4c - Typical-Urban-Blend |  | Boise Air Terminal Uo | 101280 | 1 | 1.8896 | 47.5 | 586 | 126.5 | 376.5 | 211260 | 109975 | 0 | 0 | 0 | 6.441 | 0.0004001% | 0.1339% | 0.0007603% | 0% | 1.654% | 0% | 2.68% | 0.6049% | 7.649% | 0% | 0% | 0% | 0% | 0% | 12.72% | 3 | 980.5 | 5 | 0 | 0 | 0 | 483.3334 | 4430.5 | 56025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413.518 | 0 | 686.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12 | 0 | 2140 | 3244.5 | 3224.4 | 19007.4 | 12093 | 74010 | 50168 | 16319 | 54863.6 | 7800 | 30708 | 48827 | 22422
MediumOffice | 2 - Prototype-NewHvacLoadsConstSch¦4d - Prototype-Prototype-Blend |  | Boise Air Terminal Uo | 1701420 | 0 | 31.7263 | 339.25 | 950.75 | 214.5 | 384.5 | 1842320 | 140903 | 0 | 0 | 0 | 125.457 | 23.04% | 0% | 28.71% | 0% | 0.0003801% | 0% | 5.646% | 8.618% | 13.35% | 0% | 0% | 0% | 0% | 0% | 79.37% | 168778 | 0 | 210295 | 0 | 0 | 0 | 58.3334 | 63119.1 | 97795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.095 | 0 | 1409.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575888 | 620879 | 0 | 112244 | 949 | 310.55 | 4044.5 | 17027 | 14793 | 12615 | 364975 | 59534.6 | 114349 | 38664 | 44044 | 31723
chart | [19 empty] | look at plenum for 4d, identify heating change between 0 and 1
LargeOffice | 0 - Prototype | run/Prototype Row B/datapoint_59c942e553ff6b03c8620179 | Boise Air Terminal Uo | 40275000 | 498588 | 80.7781 | 272 | 4043.75 | 48.25 | 490.5 | 36124100 | 4150930 | 0 | 0 | 0 | 2242.44 | 4643050 | 2703640 | 19714300 | 0 | 542104 | 0 | 3610060 | 2494320 | 2789530 | 531280 | 350351 | 2525220 | 371118 | 0 |  | 1360740 | 792358 | 5777700 | 0 | 0 | 0 | 363.889 | 731014 | 817531 | 155703 | 102678 | 740069 | 108764 | 0 | 0 | 0 | 0 | 0 | 5422.09 | 0 | 36095.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1428630 | 13695800 | 0 | 454767 | 116066 | 13103.2 | 165.3 | 679175 | 1307910 | 519756 | 311092 | 1144400 | 2157440 | 909375 | 768324 | 700534
LargeOffice | 1 - Prototype-NewHvac | run/Prototype Row B/datapoint_59c942ed53ff6b03c8620189 | Boise Air Terminal Uo | 44803200 | 498588 | 89.86 | 482.75 | 8760 | 266.5 | 1300 | 39820900 | 4982230 | 0 | 0 | 0 | 2208.29 | 4643050 | 2703640 | 19714300 | 0 | 542313 | 0 | 4439920 | 7274440 | 2921290 | 1023780 | 194141 | 0 | 1346260 | 0 |  | 1360740 | 792358 | 5777700 | 0 | 0 | 0 | 0 | 2131930 | 856144 | 300042 | 56897.2 | 0 | 394550 | 0 | 0 | 0 | 0 | 0 | 5424.17 | 0 | 44407.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1428630 | 13695800 | 0 | 457375 | 59599.7 | 10786.5 | 155.2 | 677451 | 1307650 | 516555 | 303725 | 560739 | 2823240 | 909501 | 763230 | 698676
LargeOffice | 2 - Prototype-NewHvacLoadsConstSch | run/Prototype Row B/datapoint_59c942f553ff6b03c8620199 | Boise Air Terminal Uo | 45426000 | 498588 | 91.1091 | 513.75 | 8760 | 301.25 | 1292.75 | 39965800 | 5460180 | 0 | 0 | 0 | 2202.77 | 4643050 | 1093460 | 21386100 | 0 | 293340 | 0 | 5166840 | 7335120 | 2929190 | 1037090 | 195535 | 0 | 1346260 | 0 |  | 1360740 | 320461 | 6267640 | 0 | 0 | 0 | 0 | 2149710 | 858461 | 303942 | 57305.6 | 0 | 394550 | 0 | 0 | 0 | 0 | 0 | 2933.97 | 0 | 51678.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1428630 | 13696500 | 0 | 458399 | 77816.6 | 22333.5 | 154.7 | 678040 | 1309970 | 517029 | 414574 | 684470 | 2821910 | 908397 | 759624 | 697540
LargeOffice | 3b - Typical-Bar-Sliced | run/Prototype Row B/datapoint_59c9430753ff6b03c86201a9 | Boise Air Terminal Uo | 42159600 | 498584 | 84.5587 | 1687.75 | 8760 | 755.25 | 1423.75 | 36992000 | 5167640 | 0 | 0 | 0 | 2039.15 | 4643010 | 1098360 | 21379600 | 0 | 210510 | 0 | 4957210 | 6355260 | 2438350 | 943922 | 133386 | 0 | 0 | 0 |  | 1360730 | 321897 | 6265750 | 0 | 0 | 0 | 22.2222 | 1862540 | 714611 | 276636 | 39091.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2105.51 | 0 | 49580.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4643010 | 19708600 | 0 | 1561500 | 245375 | 113736 | 722.7 | 3776610 | 1978520 | 347988 | 1718270 | 919230 | 4076140 | 5068952 | 1164010 | 634102
LargeOffice | 4b - Typical-Bar-Blend | run/Prototype Row B/datapoint_59c9431053ff6b03c86201b9 | Boise Air Terminal Uo | 39853800 | 498584 | 79.9341 | 445 | 1541.25 | 250.25 | 791.5 | 38026200 | 1827610 | 0 | 0 | 0 | 2227.95 | 4643010 | 1098360 | 21379600 | 0 | 210472 | 0 | 1617140 | 5853140 | 2440200 | 1057010 | 230547 | 0 | 1324310 | 0 |  | 1360730 | 321897 | 6265750 | 0 | 0 | 0 | 0 | 1715390 | 715153 | 309778 | 67566.7 | 0 | 388117 | 0 | 0 | 0 | 0 | 0 | 2105.13 | 0 | 16174.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1428620 | 6064180 | 0 | 464119 | 94103.3 | 43947.5 | 340.2 | 874102 | 455175 | 348333 | 757367 | 143924 | 1323929 | 1199060 | 271625 | 668626
LargeOffice | 4c - Typical-Urban-Blend | run/Prototype Row B/datapoint_59c9432b53ff6b03c86201cb | Boise Air Terminal Uo | 36900800 | 498579 | 74.012 | 333.75 | 3201.75 | 175.5 | 1480.75 | 35761900 | 1138930 | 0 | 0 | 0 | 2194.57 | 4642970 | 1098360 | 21379400 | 0 | 210472 | 0 | 928463 | 5929440 | 1248000 | 1232480 | 231201 | 0 | 0 | 0 |  | 1360720 | 321897 | 6265690 | 0 | 0 | 0 | 0 | 1737750 | 365753 | 361206 | 67758.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2105.13 | 0 | 9286.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4642970 | 19708400 | 0 | 1484080 | 132479 | 121140 | 445.7 | 3155470 | 4001360 | 322624 | 2377050 | 59532.6 | 1326620 | 4948270 | 3021030 | 655602
LargeOffice | 4d - Prototype-Prototype-Blend | run/Prototype Row B/datapoint_59c991be45b421004abe3aac | Boise Air Terminal Uo | 70327100 | 498588 | 141.052 | 160.25 | 1425.5 | 108.25 | 718.75 | 68355100 | 1972010 | 0 | 0 | 0 | 3670.82 | 8928940 | 1093460 | 41127000 | 0 | 293274 | 0 | 1678740 | 10624600 | 4439290 | 1736890 | 404832 | 0 | 0 | 0 |  | 2616810 | 320461 | 12053100 | 0 | 0 | 0 | 0 | 3113770 | 1301030 | 509033 | 118644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2933.3 | 0 | 16790.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2500100 | 10615800 | 0 | 547119 | 149630 | 16666.9 | 132.7 | 618661 | 1267500 | 460008 | 1753730 | 56046.3 | 1160033 | 1040210 | 846680 | 837077
| bonus - 0 ot 2 error as single step | [15 empty] | 0 | 1610180 | 1671800 | 0 | 248764 | 0 | 1556780 | 4840800 | 139660 | 505810 | 154816 | 2525220 | 975142 | 0 | 35.33%
LargeOffice | 0 - Prototype¦1 - Prototype-NewHvac |  | Boise Air Terminal Uo | 4528200 | 0 | 9.0819 | 210.75 | 4716.25 | 218.25 | 809.5 | 3696800 | 831300 | 0 | 0 | 0 | 34.15 | 0% | 0% | 0% | 0% | 0.0005189% | 0% | 2.06% | 11.87% | 0.3272% | 1.223% | 0.3879% | 6.27% | 2.421% | 0% | 24.56% | 0 | 0 | 0 | 0 | 0 | 0 | 363.889 | 1400916 | 38613 | 144339 | 45780.8 | 740069 | 285786 | 0 | 0 | 0 | 0 | 0 | 2.08 | 0 | 8312.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2608 | 56466.3 | 2316.7 | 10.1 | 1724 | 260 | 3201 | 7367 | 583661 | 665800 | 126 | 5094 | 1858
LargeOffice | 1 - Prototype-NewHvac¦2 - Prototype-NewHvacLoadsConstSch |  | Boise Air Terminal Uo | 622800 | 0 | 1.2491 | 31 | 0 | 34.75 | 7.25 | 144900 | 477950 | 0 | 0 | 0 | 5.52 | 0% | 3.594% | 3.731% | 0% | 0.5557% | 0% | 1.622% | 0.1354% | 0.01763% | 0.02971% | 0.003111% | 0% | 0% | 0% | 9.689% | 0 | 471897 | 489940 | 0 | 0 | 0 | 0 | 17780 | 2317 | 3900 | 408.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2490.2 | 0 | 7270.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 700 | 0 | 1024 | 18216.9 | 11547 | 0.5 | 589 | 2320 | 474 | 110849 | 123731 | 1330 | 1104 | 3606 | 1136
LargeOffice | 2 - Prototype-NewHvacLoadsConstSch¦3b - Typical-Bar-Sliced |  | Boise Air Terminal Uo | 3266400 | 4 | 6.5504 | 1174 | 0 | 454 | 131 | 2973800 | 292540 | 0 | 0 | 0 | 163.62 | 8.8055e-07 | 0.01079% | 0.01431% | 0% | 0.1823% | 0% | 0.4615% | 2.157% | 1.081% | 0.2051% | 0.1368% | 0% | 2.964% | 0% | 7.212% | 10 | 1436 | 1890 | 0 | 0 | 0 | 22.2222 | 287170 | 143850 | 27306 | 18213.9 | 0 | 394550 | 0 | 0 | 0 | 0 | 0 | 828.46 | 0 | 2097.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3214380 | 6012100 | 0 | 1103101 | 167558.4 | 91402.5 | 568 | 3098570 | 668550 | 169041 | 1303696 | 234760 | 1254230 | 4160555 | 404386 | 63438
LargeOffice | 2 - Prototype-NewHvacLoadsConstSch¦4b - Typical-Bar-Blend |  | Boise Air Terminal Uo | 5572200 | 4 | 11.175 | 68.75 | 7218.75 | 51 | 501.25 | 1939600 | 3632570 | 0 | 0 | 0 | 25.18 | 8.8055e-07 | 0.01079% | 0.01431% | 0% | 0.1824% | 0% | 7.814% | 3.262% | 1.076% | 0.04385% | 0.07707% | 0% | 0.04832% | 0% | 12.53% | 10 | 1436 | 1890 | 0 | 0 | 0 | 0 | 434320 | 143308 | 5836 | 10261.1 | 0 | 6433 | 0 | 0 | 0 | 0 | 0 | 828.84 | 0 | 35503.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7632320 | 0 | 5720 | 16286.7 | 21614 | 185.5 | 196062 | 854795 | 168696 | 342793 | 540546 | 1497981 | 290663 | 487999 | 28914
LargeOffice | 2 - Prototype-NewHvacLoadsConstSch¦4c - Typical-Urban-Blend |  | Boise Air Terminal Uo | 8525200 | 9 | 17.0971 | 180 | 5558.25 | 125.75 | 188 | 4203900 | 4321250 | 0 | 0 | 0 | 8.2 | 0.0001761% | 0.01079% | 0.01475% | 0% | 0.1824% | 0% | 9.33% | 3.094% | 3.701% | 0.4301% | 0.07851% | 0% | 2.964% | 0% | 19.81% | 20 | 1436 | 1950 | 0 | 0 | 0 | 0 | 411960 | 492708 | 57264 | 10452.7 | 0 | 394550 | 0 | 0 | 0 | 0 | 0 | 828.84 | 0 | 42391.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3214340 | 6011900 | 0 | 1025681 | 54662.4 | 98806.5 | 291 | 2477430 | 2691390 | 194405 | 1962476 | 624937.4 | 1495290 | 4039873 | 2261406 | 41938
LargeOffice | 2 - Prototype-NewHvacLoadsConstSch¦4d - Prototype-Prototype-Blend |  | Boise Air Terminal Uo | 24901100 | 0 | 49.9429 | 353.5 | 7334.5 | 193 | 574 | 28389300 | 3488170 | 0 | 0 | 0 | 1468.05 | 9.435% | 0% | 43.46% | 0% | 0.0001453% | 0% | 7.679% | 7.241% | 3.324% | 1.541% | 0.4607% | 0% | 2.964% | 0% | 76.1% | 1256070 | 0 | 5785460 | 0 | 0 | 0 | 0 | 964060 | 442569 | 205091 | 61338.4 | 0 | 394550 | 0 | 0 | 0 | 0 | 0 | 0.67 | 0 | 34887.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1071470 | 3080700 | 0 | 88720 | 71813.4 | 5666.6 | 22 | 59379 | 42470 | 57021 | 1339156 | 628423.7 | 1661877 | 131813 | 87056 | 139537
chart | [19 empty] | look at plenum for 4d, identify heating change between 0 and 1, what is going on with heat gains and losses in 3 and 4s
SmallHotel | 0 - Prototype | run/Prototype Row B/datapoint_59c942e553ff6b03c8620181 | Boise Air Terminal Uo | 4215160 | 43201.8 | 97.5691 | 2127 | 2792.25 | 1658.5 | 763.5 | 2867330 | 1347830 | 0 | 0 | 0 | 178.801 | 473890 | 90165.8 | 959352 | 0 | 763125 | 0 | 274147 | 461653 | 1192470 | 350.692 | 0 | 0 | 0 | 0 |  | 138883 | 26425 | 164103 | 0 | 0 | 0 | 26038.9 | 135297 | 349478 | 102.778 | 0 | 0 | 0 | 0 | 0 | 0 | 3994.87 | 0 | 7632.73 | 0 | 1853.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 473890 | 559945 | 399411 | 191512 | 50219.1 | 8162.45 | 3769.6 | 377721 | 237939 | 119583 | 190905 | 147892 | 440013 | 521463 | 131204 | 184854
SmallHotel | 1 - Prototype-NewHvac | run/Prototype Row B/datapoint_59c942ed53ff6b03c8620191 | Boise Air Terminal Uo | 4885380 | 43201.8 | 113.083 | 3.75 | 29 | 0 | 20 | 3190560 | 1694820 | 0 | 0 | 0 | 170.059 | 473890 | 90165.8 | 959352 | 0 | 763107 | 0 | 532304 | 573572 | 1492190 | 805.645 | 0 | 0 | 0 | 0 |  | 138883 | 26425 | 164103 | 0 | 0 | 0 | 0 | 168097 | 437317 | 236.111 | 0 | 0 | 0 | 0 | 0 | 0 | 3994.87 | 0 | 7632.54 | 0 | 5324.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 473890 | 559945 | 399411 | 191906 | 56625.6 | 11330.1 | 6360.5 | 381374 | 241999 | 119923 | 180932 | 201226 | 272250 | 507941 | 122872 | 183905
SmallHotel | 2 - Prototype-NewHvacLoadsConstSch | run/Prototype Row B/datapoint_59c942f553ff6b03c86201a1 | Boise Air Terminal Uo | 4877650 | 43201.8 | 112.904 | 5.75 | 40 | 0.5 | 28.25 | 3421560 | 1456080 | 0 | 0 | 0 | 181.324 | 473890 | 270479 | 1085490 | 0 | 486211 | 0 | 570463 | 550748 | 1439630 | 739.297 | 0 | 0 | 0 | 0 |  | 138883 | 79269.4 | 201069 | 0 | 0 | 0 | 0 | 161408 | 421914 | 216.667 | 0 | 0 | 0 | 0 | 0 | 0 | 3994.87 | 0 | 4863.05 | 0 | 5705.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 473890 | 566252 | 399411 | 192004 | 57783.6 | 19992.4 | 4780.2 | 387192 | 242010 | 119970 | 265870 | 306357 | 268593 | 485646 | 122866 | 183952
SmallHotel | 3b - Typical-Bar-Sliced | run/Prototype Row B/datapoint_59c9430753ff6b03c86201b1 | Boise Air Terminal Uo | 4702880 | 43196 | 108.873 | 37.25 | 142.25 | 10.5 | 88.75 | 3273440 | 1429440 | 0 | 0 | 0 | 173.398 | 473757 | 268962 | 1088840 | 0 | 451730 | 0 | 577922 | 504466 | 1336430 | 758.254 | 0 | 0 | 0 | 0 |  | 138844 | 78825 | 201944 | 0 | 0 | 0 | 0 | 147844 | 391669 | 222.222 | 0 | 0 | 0 | 0 | 0 | 0 | 3998.57 | 0 | 4518.17 | 0 | 5780.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 473754 | 569266 | 399784 | 191098 | 57499.8 | 21371 | 5519.8 | 316740 | 196616 | 103718 | 267432 | 273445 | 245860 | 427093 | 124459 | 179389
SmallHotel | 4b - Typical-Bar-Blend | run/Prototype Row B/datapoint_59c9431053ff6b03c86201c1 | Boise Air Terminal Uo | 4986570 | 43196 | 115.441 | 0.5 | 10 | 0.5 | 10 | 3888370 | 1098200 | 0 | 0 | 0 | 205.755 | 473757 | 268962 | 1088840 | 0 | 451692 | 0 | 246726 | 655965 | 1800190 | 426.518 | 0 | 0 | 0 | 0 |  | 138844 | 78825 | 201944 | 0 | 0 | 0 | 0 | 192244 | 527583 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 3998.57 | 0 | 4517.79 | 0 | 2467.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355316 | 426950 | 299838 | 148620 | 90133.4 | 24844.7 | 1164.6 | 238087 | 150610 | 103271 | 240427 | 341874 | 118364 | 317213 | 91246.4 | 178203
SmallHotel | 4c - Typical-Urban-Blend | run/Prototype Row B/datapoint_59c9432b53ff6b03c86201d3 | Boise Air Terminal Uo | 5320980 | 43201.2 | 123.167 | 0 | 0.75 | 0 | 0.75 | 4195460 | 1125530 | 0 | 0 | 0 | 221.298 | 473814 | 268962 | 1088980 | 0 | 451692 | 0 | 274014 | 704645 | 2058430 | 445.474 | 0 | 0 | 0 | 0 |  | 138861 | 78825 | 201969 | 0 | 0 | 0 | 0 | 206511 | 603267 | 130.556 | 0 | 0 | 0 | 0 | 0 | 0 | 3999.04 | 0 | 4517.79 | 0 | 2740.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 473810 | 569334 | 399831 | 198183 | 91003.8 | 29171.3 | 1303.4 | 243182 | 529926 | 98816.4 | 282149 | 469235 | 147801 | 332944 | 319702 | 178160
SmallHotel | 4d - Prototype-Prototype-Blend | run/Prototype Row B/datapoint_59c991be45b421004abe3ab4 | Boise Air Terminal Uo | 5099760 | 43201.8 | 118.045 | 54.75 | 106.5 | 54.75 | 106.5 | 4018980 | 1080780 | 0 | 0 | 0 | 215.457 | 473890 | 270479 | 1085490 | 0 | 486164 | 0 | 195212 | 688144 | 1899990 | 388.605 | 0 | 0 | 0 | 0 |  | 138883 | 79269.4 | 201069 | 0 | 0 | 0 | 0 | 201675 | 556833 | 113.889 | 0 | 0 | 0 | 0 | 0 | 0 | 3994.87 | 0 | 4862.58 | 0 | 1952.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 473890 | 566252 | 399411 | 198263 | 90776.2 | 31002.7 | 672.9 | 388378 | 246126 | 118856 | 300053 | 286234 | 118229 | 487055 | 121051 | 187427
| bonus - 0 ot 2 error as single step | [15 empty] | 0 | 180313.2 | 126138 | 0 | 276914 | 0 | 296316 | 89095 | 247160 | 388.605 | 0 | 0 | 0 | 0 | 28.86%
SmallHotel | 0 - Prototype¦1 - Prototype-NewHvac |  | Boise Air Terminal Uo | 670220 | 0 | 15.5139 | 2123.25 | 2763.25 | 1658.5 | 743.5 | 323230 | 346990 | 0 | 0 | 0 | 8.742 | 0% | 0% | 0% | 0% | 0.000427% | 0% | 6.124% | 2.655% | 7.111% | 0.01079% | 0% | 0% | 0% | 0% | 15.9% | 0 | 0 | 0 | 0 | 0 | 0 | 26038.9 | 32800 | 87839 | 133.333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19 | 0 | 3470.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 394 | 6406.5 | 3167.65 | 2590.9 | 3653 | 4060 | 340 | 9973 | 53334 | 167763 | 13522 | 8332 | 949
SmallHotel | 1 - Prototype-NewHvac¦2 - Prototype-NewHvacLoadsConstSch |  | Boise Air Terminal Uo | 7730 | 0 | 0.179 | 2 | 11 | 0.5 | 8.25 | 231000 | 238740 | 0 | 0 | 0 | 11.265 | 0% | 3.691% | 2.582% | 0% | 5.668% | 0% | 0.7811% | 0.4672% | 1.076% | 0.001358% | 0% | 0% | 0% | 0% | 14.27% | 0 | 52844.4 | 36966 | 0 | 0 | 0 | 0 | 6689 | 15403 | 19.444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2769.49 | 0 | 381.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6307 | 0 | 98 | 1158 | 8662.3 | 1580.3 | 5818 | 11 | 47 | 84938 | 105131 | 3657 | 22295 | 6 | 47
SmallHotel | 2 - Prototype-NewHvacLoadsConstSch¦3b - Typical-Bar-Sliced |  | Boise Air Terminal Uo | 174770 | 5.8 | 4.031 | 31.5 | 102.25 | 10 | 60.5 | 148120 | 26640 | 0 | 0 | 0 | 7.926 | 0.002727% | 0.0311% | 0.06868% | 0% | 0.7069% | 0% | 0.1529% | 0.9489% | 2.116% | 0.0003887% | 0% | 0% | 0% | 0% | 4.027% | 39 | 444.4 | 875 | 0 | 0 | 0 | 0 | 13564 | 30245 | 5.555 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 344.88 | 0 | 74.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 3014 | 373 | 906 | 283.8 | 1378.6 | 739.6 | 70452 | 45394 | 16252 | 1562 | 32912 | 22733 | 58553 | 1593 | 4563
SmallHotel | 2 - Prototype-NewHvacLoadsConstSch¦4b - Typical-Bar-Blend |  | Boise Air Terminal Uo | 108920 | 5.8 | 2.537 | 5.25 | 30 | 0 | 18.25 | 466810 | 357880 | 0 | 0 | 0 | 24.431 | 0.002727% | 0.0311% | 0.06868% | 0% | 0.7077% | 0% | 6.637% | 2.157% | 7.392% | 0.006412% | 0% | 0% | 0% | 0% | 17% | 39 | 444.4 | 875 | 0 | 0 | 0 | 0 | 30836 | 105669 | 91.667 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 345.26 | 0 | 3237.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118574 | 139302 | 99573 | 43384 | 32349.8 | 4852.3 | 3615.6 | 149105 | 91400 | 16699 | 25443 | 35517 | 150229 | 168433 | 31619.6 | 5749
SmallHotel | 2 - Prototype-NewHvacLoadsConstSch¦4c - Typical-Urban-Blend |  | Boise Air Terminal Uo | 443330 | 0.6 | 10.263 | 5.75 | 39.25 | 0.5 | 27.5 | 773900 | 330550 | 0 | 0 | 0 | 39.974 | 0.001558% | 0.0311% | 0.07155% | 0% | 0.7077% | 0% | 6.078% | 3.155% | 12.69% | 0.006024% | 0% | 0% | 0% | 0% | 22.74% | 22 | 444.4 | 900 | 0 | 0 | 0 | 0 | 45103 | 181353 | 86.111 | 0 | 0 | 0 | 0 | 0 | 0 | 4.17 | 0 | 345.26 | 0 | 2965.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 3082 | 420 | 6179 | 33220.2 | 9178.9 | 3476.8 | 144010 | 287916 | 21153.6 | 16279 | 162878 | 120792 | 152702 | 196836 | 5792
SmallHotel | 2 - Prototype-NewHvacLoadsConstSch¦4d - Prototype-Prototype-Blend |  | Boise Air Terminal Uo | 222110 | 0 | 5.141 | 49 | 66.5 | 54.25 | 78.25 | 597420 | 375300 | 0 | 0 | 0 | 34.133 | 0% | 0% | 0% | 0% | 0.0009636% | 0% | 7.693% | 2.817% | 9.438% | 0.00719% | 0% | 0% | 0% | 0% | 19.96% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40267 | 134919 | 102.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.47 | 0 | 3753.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6259 | 32992.6 | 11010.3 | 4107.3 | 1186 | 4116 | 1114 | 34183 | 20123 | 150364 | 1409 | 1815 | 3475
chart | [19 empty] | look at change in swh from 1 to 2, look at drop in gans and losses in blended bar
LargeHotel | 3b - Typical-Bar-Sliced | run/Prototype Row B/datapoint_59c9430753ff6b03c86201a8 | Boise Air Terminal Uo | 15426000 | 122117 | 126.321 | 978 | 5374.5 | 964.25 | 1732.25 | 8411750 | 7014240 | 0 | 0 | 0 | 541.206 | 1400690 | 357062 | 4502770 | 0 | 1315330 | 0 | 3642760 | 1407300 | 2751490 | 5061.34 | 0 | 0 | 43514.3 | 0 |  | 410503 | 104644 | 717036 | 0 | 0 | 0 | 0 | 412439 | 806383 | 1483.33 | 0 | 0 | 12752.8 | 0 | 0 | 0 | 20565.3 | 0 | 13155.9 | 0 | 36434.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1400690 | 1559060 | 1093350 | 1020060 | 125911 | 30387.9 | 194.7 | 1088110 | 1130750 | 176530 | 501109 | 531180 | 809494 | 1518740 | 762763 | 319209
LargeHotel | 4b - Typical-Bar-Blend | run/Prototype Row B/datapoint_59c9431053ff6b03c86201b8 | Boise Air Terminal Uo | 14305900 | 122117 | 117.149 | 2.25 | 1.25 | 2.25 | 1.25 | 8740920 | 5564960 | 0 | 0 | 0 | 565.452 | 1400690 | 357062 | 4502770 | 0 | 1315210 | 0 | 2193610 | 1013010 | 3521520 | 2018.85 | 0 | 0 | 0 | 0 |  | 410503 | 104644 | 717036 | 0 | 0 | 0 | 0 | 296883 | 1032060 | 591.667 | 0 | 0 | 0 | 0 | 0 | 0 | 20565.3 | 0 | 13154.6 | 0 | 21940.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800396 | 890892 | 624774 | 559609 | 182438 | 14578.4 | 239.1 | 469855 | 487901 | 185122 | 263474 | 771999 | 400913 | 662096 | 326071 | 322232
LargeHotel | 4c - Typical-Urban-Blend | run/Prototype Row B/datapoint_59c9432b53ff6b03c86201ca | Boise Air Terminal Uo | 17251500 | 149097 | 115.707 | 0 | 1.75 | 0 | 1.75 | 10364500 | 6887100 | 0 | 0 | 0 | 660.218 | 1710160 | 357062 | 5497590 | 0 | 1315210 | 0 | 3061470 | 1094070 | 4213240 | 2748.67 | 0 | 0 | 0 | 0 |  | 501197 | 104644 | 875456 | 0 | 0 | 0 | 0 | 320642 | 1234780 | 805.556 | 0 | 0 | 0 | 0 | 0 | 0 | 25108.9 | 0 | 13154.6 | 0 | 30620.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1710160 | 1903510 | 1334920 | 1192050 | 225185 | 38290.1 | 333.1 | 1230130 | 1499610 | 206005 | 699887 | 953664 | 498756 | 1822020 | 1052810 | 386848
| bonus - 0 ot 2 error as single step | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
LargeHotel | 0 - Prototype¦1 - Prototype-NewHvac | [15 empty] | NaN% | NaN% | NaN% | NaN% | NaN% | NaN% | NaN% | NaN% | NaN% | NaN% | NaN% | NaN% | NaN% | NaN%
LargeHotel | 1 - Prototype-NewHvac¦2 - Prototype-NewHvacLoadsConstSch | [15 empty] | NaN% | NaN% | NaN% | NaN% | NaN% | NaN% | NaN% | NaN% | NaN% | NaN% | NaN% | NaN% | NaN% | NaN%
LargeHotel | 2 - Prototype-NewHvacLoadsConstSch¦3b - Typical-Bar-Sliced | [15 empty] | Infinity% | Infinity% | Infinity% | NaN% | Infinity% | NaN% | Infinity% | Infinity% | Infinity% | Infinity% | NaN% | NaN% | Infinity% | NaN%
LargeHotel | 2 - Prototype-NewHvacLoadsConstSch¦4b - Typical-Bar-Blend | [15 empty] | Infinity% | Infinity% | Infinity% | NaN% | Infinity% | NaN% | Infinity% | Infinity% | Infinity% | Infinity% | NaN% | NaN% | NaN% | NaN%
LargeHotel | 2 - Prototype-NewHvacLoadsConstSch¦4c - Typical-Urban-Blend | [15 empty] | Infinity% | Infinity% | Infinity% | NaN% | Infinity% | NaN% | Infinity% | Infinity% | Infinity% | Infinity% | NaN% | NaN% | NaN% | NaN%
LargeHotel | 2 - Prototype-NewHvacLoadsConstSch¦4d - Prototype-Prototype-Blend | [15 empty] | NaN% | NaN% | NaN% | NaN% | NaN% | NaN% | NaN% | NaN% | NaN% | NaN% | NaN% | NaN% | NaN% | NaN%
chart | [19 empty] | prototypes should run in 2.3, look at drop in gans and losses in blended bar
MidriseApartment | 0 - Prototype | run/Prototype Row B/datapoint_59c942e553ff6b03c862017f | Boise Air Terminal Uo | 1832520 | 33740.7 | 54.3119 | 0.75 | 0 | 0 | 0 | 1472350 | 360180 | 0 | 0 | 0 | 126.066 | 113065 | 69029.5 | 490751 | 0 | 341499 | 0 | 360180 | 153338 | 304657 | 0 | 0 | 0 | 0 | 0 |  | 33136.1 | 20230.6 | 143825 | 0 | 100083 | 0 | 0 | 44938.9 | 89286.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3602.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89715.9 | 281478 | 0 | 83935.8 | 13501 | 7105.26 | 2344 | 222178 | 254114 | 95265.7 | 151376 | 166127 | 93276.5 | 294789 | 162949 | 155282
MidriseApartment | 1 - Prototype-NewHvac | run/Prototype Row B/datapoint_59c942ed53ff6b03c862018f | Boise Air Terminal Uo | 2050170 | 33740.7 | 60.7625 | 7 | 40.25 | 7 | 39 | 1783070 | 267085 | 0 | 0 | 0 | 133.062 | 113065 | 69029.5 | 490751 | 0 | 341499 | 0 | 267085 | 187232 | 581258 | 236.954 | 0 | 0 | 0 | 0 |  | 33136.1 | 20230.6 | 143825 | 0 | 100083 | 0 | 0 | 54872.2 | 170350 | 69.4444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2671.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89715.9 | 281478 | 0 | 83146.3 | 13570.4 | 8511.74 | 412.1 | 221817 | 253296 | 95071.4 | 163880 | 143819 | 108052 | 295971 | 165377 | 156118
MidriseApartment | 2 - Prototype-NewHvacLoadsConstSch | run/Prototype Row B/datapoint_59c942f553ff6b03c862019f | Boise Air Terminal Uo | 2260780 | 33740.7 | 67.0046 | 8 | 48.25 | 8 | 45.5 | 1513350 | 747430 | 0 | 0 | 0 | 122.571 | 113065 | 208747 | 490808 | 0 | 492609 | 0 | 265247 | 171944 | 518115 | 236.954 | 0 | 0 | 0 | 0 |  | 33136.1 | 61177.8 | 143842 | 0 | 3055.56 | 0 | 0 | 50391.7 | 151844 | 69.4444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4822.76 | 0 | 2652.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89715.9 | 281480 | 0 | 83307 | 13550.3 | 6303.35 | 329.1 | 222063 | 253869 | 95073.1 | 128320 | 147670 | 130764 | 295370 | 164380 | 156120
MidriseApartment | 3b - Typical-Bar-Sliced | run/Prototype Row B/datapoint_59c9430753ff6b03c86201af | Boise Air Terminal Uo | 2157300 | 33740 | 63.9389 | 3.75 | 96.25 | 3.75 | 84.5 | 1402510 | 754785 | 0 | 0 | 0 | 81.4061 | 113103 | 208747 | 490799 | 0 | 482183 | 0 | 272602 | 135547 | 454071 | 255.911 | 0 | 0 | 0 | 0 |  | 33147.2 | 61177.8 | 143839 | 0 | 0 | 0 | 0 | 39725 | 133075 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4822.76 | 0 | 2726.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113100 | 374072 | 0 | 111529 | 13402.3 | 8760.2 | 140.8 | 309851 | 255290 | 91531.3 | 177649 | 126104 | 143596 | 416388 | 170497 | 153637
MidriseApartment | 4b - Typical-Bar-Blend | run/Prototype Row B/datapoint_59c9431053ff6b03c86201bf | Boise Air Terminal Uo | 2269950 | 33740 | 67.2776 | 0.25 | 54.25 | 0.25 | 54.25 | 1492660 | 777286 | 0 | 0 | 0 | 86.6489 | 113103 | 208747 | 490799 | 0 | 482183 | 0 | 295103 | 167062 | 512684 | 274.867 | 0 | 0 | 0 | 0 |  | 33147.2 | 61177.8 | 143839 | 0 | 0 | 0 | 0 | 48961.1 | 150253 | 80.5556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4822.76 | 0 | 2951.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84825 | 280554 | 0 | 83995.1 | 13335.5 | 7996.38 | 165.1 | 231419 | 190956 | 92271.7 | 162486 | 133896 | 121821 | 309857 | 125953 | 152229
MidriseApartment | 4c - Typical-Urban-Blend | run/Prototype Row B/datapoint_59c9432b53ff6b03c86201d1 | Boise Air Terminal Uo | 2331370 | 33687.8 | 69.2053 | 0 | 23.75 | 0 | 23.75 | 1538540 | 792830 | 0 | 0 | 0 | 91.2637 | 112923 | 208747 | 490031 | 0 | 482183 | 0 | 310657 | 189980 | 536578 | 274.867 | 0 | 0 | 0 | 0 |  | 33094.4 | 61177.8 | 143614 | 0 | 0 | 0 | 0 | 55677.8 | 157256 | 80.5556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4822.76 | 0 | 3107.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112925 | 373493 | 0 | 111315 | 13441 | 9432.42 | 104.3 | 248534 | 496129 | 89055.7 | 193496 | 166219 | 141433 | 339771 | 330339 | 152030
MidriseApartment | 4d - Prototype-Prototype-Blend | run/Prototype Row B/datapoint_59c991be45b421004abe3ab2 | Boise Air Terminal Uo | 2283030 | 33740.7 | 67.6639 | 9.5 | 40.75 | 9.5 | 40.75 | 1515080 | 767950 | 0 | 0 | 0 | 123.02 | 113065 | 208747 | 490808 | 0 | 492609 | 0 | 285767 | 171394 | 520380 | 255.911 | 0 | 0 | 0 | 0 |  | 33136.1 | 61177.8 | 143842 | 0 | 3055.56 | 0 | 0 | 50230.6 | 152508 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4822.76 | 0 | 2858.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84801.9 | 280563 | 0 | 83915.5 | 13397.1 | 7855.62 | 106.1 | 221700 | 253570 | 95054.4 | 160265 | 144794 | 131268 | 294807 | 163635 | 155093
| bonus - 0 ot 2 error as single step | [15 empty] | 0 | 139717.5 | 57 | 0 | 151110 | 0 | 94933 | 18606 | 213458 | 236.954 | 0 | 0 | 0 | 0 | 33.73%
MidriseApartment | 0 - Prototype¦1 - Prototype-NewHvac |  | Boise Air Terminal Uo | 217650 | 0 | 6.4506 | 6.25 | 40.25 | 7 | 39 | 310720 | 93095 | 0 | 0 | 0 | 6.996 | 0% | 0% | 0% | 0% | 0% | 0% | 5.08% | 1.85% | 15.09% | 0.01293% | 0% | 0% | 0% | 0% | 22.04% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9933.3 | 81063.9 | 69.4444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 931.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 789.5 | 69.4 | 1406.48 | 1931.9 | 361 | 818 | 194.3 | 12504 | 22308 | 14775.5 | 1182 | 2428 | 836
MidriseApartment | 1 - Prototype-NewHvac¦2 - Prototype-NewHvacLoadsConstSch |  | Boise Air Terminal Uo | 210610 | 0 | 6.2421 | 1 | 8 | 1 | 6.5 | 269720 | 480345 | 0 | 0 | 0 | 10.491 | 0% | 6.815% | 0.00278% | 0% | 7.371% | 0% | 0.08965% | 0.7457% | 3.08% | 0% | 0% | 0% | 0% | 0% | 18.1% | 0 | 40947.2 | 17 | 0 | 97027.44 | 0 | 0 | 4480.5 | 18506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4822.76 | 0 | 18.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 160.7 | 20.1 | 2208.39 | 83 | 246 | 573 | 1.7 | 35560 | 3851 | 22712 | 601 | 997 | 2
MidriseApartment | 2 - Prototype-NewHvacLoadsConstSch¦3b - Typical-Bar-Sliced |  | Boise Air Terminal Uo | 103480 | 0.7 | 3.0657 | 4.25 | 48 | 4.25 | 39 | 110840 | 7355 | 0 | 0 | 0 | 41.1649 | 0.001681% | 0% | 0.0003981% | 0% | 0.4612% | 0% | 0.3253% | 1.61% | 2.833% | 0.0008385% | 0% | 0% | 0% | 0% | 5.232% | 11.1 | 0 | 3 | 0 | 3055.56 | 0 | 0 | 10666.7 | 18769 | 5.5556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23384.1 | 92592 | 0 | 28222 | 148 | 2456.85 | 188.3 | 87788 | 1421 | 3541.8 | 49329 | 21566 | 12832 | 121018 | 6117 | 2483
MidriseApartment | 2 - Prototype-NewHvacLoadsConstSch¦4b - Typical-Bar-Blend |  | Boise Air Terminal Uo | 9170 | 0.7 | 0.273 | 7.75 | 6 | 7.75 | 8.75 | 20690 | 29856 | 0 | 0 | 0 | 35.9221 | 0.001681% | 0% | 0.0003981% | 0% | 0.4612% | 0% | 1.321% | 0.2159% | 0.2402% | 0.001677% | 0% | 0% | 0% | 0% | 2.242% | 11.1 | 0 | 3 | 0 | 3055.56 | 0 | 0 | 1430.6 | 1591 | 11.1112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 298.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4890.9 | 926 | 0 | 688.1 | 214.8 | 1693.03 | 164 | 9356 | 62913 | 2801.4 | 34166 | 13774 | 8943 | 14487 | 38427 | 3891
MidriseApartment | 2 - Prototype-NewHvacLoadsConstSch¦4c - Typical-Urban-Blend |  | Boise Air Terminal Uo | 70590 | 52.9 | 2.2007 | 8 | 24.5 | 8 | 21.75 | 25190 | 45400 | 0 | 0 | 0 | 31.3073 | 0.006281% | 0% | 0.03437% | 0% | 0.4612% | 0% | 2.009% | 0.7978% | 0.8167% | 0.001677% | 0% | 0% | 0% | 0% | 4.127% | 41.7 | 0 | 228 | 0 | 3055.56 | 0 | 0 | 5286.1 | 5412 | 11.1112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 454.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23209.1 | 92013 | 0 | 28008 | 109.3 | 3129.07 | 224.8 | 26471 | 242260 | 6017.4 | 65176 | 18549 | 10669 | 44401 | 165959 | 4090
MidriseApartment | 2 - Prototype-NewHvacLoadsConstSch¦4d - Prototype-Prototype-Blend |  | Boise Air Terminal Uo | 22250 | 0 | 0.6593 | 1.5 | 7.5 | 1.5 | 4.75 | 1730 | 20520 | 0 | 0 | 0 | 0.449 | 0% | 0% | 0% | 0% | 0% | 0% | 0.9077% | 0.02433% | 0.1002% | 0.0008385% | 0% | 0% | 0% | 0% | 1.033% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161.1 | 664 | 5.5556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4914 | 917 | 0 | 608.5 | 153.2 | 1552.27 | 223 | 363 | 299 | 18.7 | 31945 | 2876 | 504 | 563 | 745 | 1027
chart | [19 empty] | is increase in ext lighting and swh too big
HighriseApartment | 0 - Prototype | run/Prototype Row B/datapoint_59c942e553ff6b03c8620180 | Boise Air Terminal Uo | 4659910 | 84351.2 | 55.2442 | 108.25 | 216.75 | 105.25 | 216.75 | 3020300 | 1639630 | 0 | 0 | 0 | 210.702 | 253190 | 201951 | 1078080 | 0 | 1089360 | 0 | 744378 | 477690 | 731667 | 46120.8 | 37486.2 | 0 | 0 | 0 |  | 74202.8 | 59186.1 | 315953 | 0 | 0 | 0 | 56891.7 | 139997 | 214431 | 13516.7 | 10986.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10895.7 | 0 | 5503.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253187 | 931284 | 0 | 283567 | 32782.5 | 30370.4 | 3959.3 | 635651 | 1244130 | 90286.6 | 651592 | 420405 | 110106 | 865637 | 847302 | 154175
HighriseApartment | 1 - Prototype-NewHvac | run/Prototype Row B/datapoint_59c942ed53ff6b03c8620190 | Boise Air Terminal Uo | 5183010 | 84351.2 | 61.4457 | 9 | 62 | 9 | 61.25 | 3442630 | 1740380 | 0 | 0 | 0 | 222.207 | 253190 | 201951 | 1078080 | 0 | 1089380 | 0 | 650999 | 508419 | 1400040 | 957.295 | 0 | 0 | 0 | 0 |  | 74202.8 | 59186.1 | 315953 | 0 | 0 | 0 | 0 | 149003 | 410311 | 280.556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10895.9 | 0 | 6511.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253187 | 931284 | 0 | 280224 | 33896.2 | 30534.5 | 3773.2 | 634380 | 1239200 | 89874.8 | 662133 | 372510 | 116580 | 869385 | 859504 | 155356
HighriseApartment | 2 - Prototype-NewHvacLoadsConstSch | run/Prototype Row B/datapoint_59c942f553ff6b03c86201a0 | Boise Air Terminal Uo | 5326530 | 84351.2 | 63.1471 | 16.5 | 76.5 | 16 | 75.75 | 3541170 | 1785370 | 0 | 0 | 0 | 225.447 | 253190 | 247968 | 1155160 | 0 | 1141290 | 0 | 644080 | 501101 | 1382790 | 957.295 | 0 | 0 | 0 | 0 |  | 74202.8 | 72672.2 | 338544 | 0 | 0 | 0 | 0 | 146858 | 405256 | 280.556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11415.1 | 0 | 6442.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253187 | 923924 | 0 | 280295 | 33904.5 | 28548.4 | 83.4 | 634386 | 1239290 | 90031.2 | 611162 | 369767 | 158765 | 869322 | 859691 | 154966
HighriseApartment | 3b - Typical-Bar-Sliced | run/Prototype Row B/datapoint_59c9430753ff6b03c86201b0 | Boise Air Terminal Uo | 4731570 | 84351 | 56.0938 | 1.5 | 152.5 | 1.5 | 149.5 | 2998350 | 1733220 | 0 | 0 | 0 | 184.431 | 253257 | 247968 | 1155180 | 0 | 1064640 | 0 | 668590 | 326703 | 1014210 | 1023.64 | 0 | 0 | 0 | 0 |  | 74222.2 | 72672.2 | 338550 | 0 | 0 | 0 | 0 | 95747.2 | 297236 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10648.4 | 0 | 6687.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253255 | 923913 | 0 | 281140 | 33214.7 | 27983.2 | 1818.4 | 741690 | 621340 | 81285.7 | 597556 | 302445 | 149742 | 1028380 | 441893 | 148687
HighriseApartment | 4b - Typical-Bar-Blend | run/Prototype Row B/datapoint_59c9431053ff6b03c86201c0 | Boise Air Terminal Uo | 5104450 | 84351 | 60.5144 | 0.25 | 68.5 | 0.25 | 68.5 | 3317060 | 1787390 | 0 | 0 | 0 | 209.361 | 253257 | 247968 | 1155180 | 0 | 1064650 | 0 | 722739 | 415258 | 1244330 | 1071.03 | 0 | 0 | 0 | 0 |  | 74222.2 | 72672.2 | 338550 | 0 | 0 | 0 | 0 | 121700 | 364678 | 313.889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10648.6 | 0 | 7228.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75976.6 | 277174 | 0 | 85710.7 | 33246.6 | 13134.9 | 172.7 | 224244 | 188327 | 82284.5 | 269693 | 311409 | 120656 | 304346 | 127029 | 146479
HighriseApartment | 4c - Typical-Urban-Blend | run/Prototype Row B/datapoint_59c9432b53ff6b03c86201d2 | Boise Air Terminal Uo | 5262940 | 84292.3 | 62.4368 | 0.5 | 26 | 0.5 | 26 | 3437090 | 1825860 | 0 | 0 | 0 | 222.354 | 253077 | 247968 | 1154370 | 0 | 1064650 | 0 | 761211 | 475766 | 1304820 | 1080.51 | 0 | 0 | 0 | 0 |  | 74169.4 | 72672.2 | 338314 | 0 | 0 | 0 | 0 | 139433 | 382406 | 316.667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10648.5 | 0 | 7613.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253079 | 923269 | 0 | 281559 | 33760.3 | 30227.8 | 105.3 | 596297 | 1212450 | 79243.2 | 631802 | 407143 | 140642 | 843339 | 864787 | 146455
HighriseApartment | 4d - Prototype-Prototype-Blend | run/Prototype Row B/datapoint_59c991be45b421004abe3ab3 | Boise Air Terminal Uo | 5383140 | 84351.2 | 63.8182 | 21.25 | 88.75 | 21.25 | 88.75 | 3568400 | 1814740 | 0 | 0 | 0 | 227.282 | 253190 | 247968 | 1155160 | 0 | 1141270 | 0 | 673471 | 501462 | 1409630 | 985.73 | 0 | 0 | 0 | 0 |  | 74202.8 | 72672.2 | 338544 | 0 | 0 | 0 | 0 | 146964 | 413122 | 288.889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11414.9 | 0 | 6736.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253187 | 923924 | 0 | 280017 | 33701.3 | 30348.9 | 84.1 | 634834 | 1241960 | 90378.7 | 637848 | 340584 | 157208 | 867825 | 856224 | 153469
| bonus - 0 ot 2 error as single step | [15 empty] | 0 | 46017 | 77080 | 0 | 51930 | 0 | 100298 | 23411 | 651123 | 45163.505 | 37486.2 | 0 | 0 | 0 | 22.16%
HighriseApartment | 0 - Prototype¦1 - Prototype-NewHvac |  | Boise Air Terminal Uo | 523100 | 0 | 6.2015 | 99.25 | 154.75 | 96.25 | 155.5 | 422330 | 100750 | 0 | 0 | 0 | 11.505 | 0% | 0% | 0% | 0% | 0.0004292% | 0% | 2.004% | 0.6594% | 14.34% | 0.9692% | 0.8044% | 0% | 0% | 0% | 18.78% | 0 | 0 | 0 | 0 | 0 | 0 | 56891.7 | 9006 | 195880 | 13236.144 | 10986.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 1007.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3343 | 1113.7 | 164.1 | 186.1 | 1271 | 4930 | 411.8 | 10541 | 47895 | 6474 | 3748 | 12202 | 1181
HighriseApartment | 1 - Prototype-NewHvac¦2 - Prototype-NewHvacLoadsConstSch |  | Boise Air Terminal Uo | 143520 | 0 | 1.7014 | 7.5 | 14.5 | 7 | 14.5 | 98540 | 44990 | 0 | 0 | 0 | 3.24 | 0% | 0.8878% | 1.487% | 0% | 1.002% | 0% | 0.1335% | 0.1412% | 0.3328% | 0% | 0% | 0% | 0% | 0% | 3.984% | 0 | 13486.1 | 22591 | 0 | 0 | 0 | 0 | 2145 | 5055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 519.2 | 0 | 69.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7360 | 0 | 71 | 8.3 | 1986.1 | 3689.8 | 6 | 90 | 156.4 | 50971 | 2743 | 42185 | 63 | 187 | 390
HighriseApartment | 2 - Prototype-NewHvacLoadsConstSch¦3b - Typical-Bar-Sliced |  | Boise Air Terminal Uo | 594960 | 0.2 | 7.0533 | 15 | 76 | 14.5 | 73.75 | 542820 | 52150 | 0 | 0 | 0 | 41.016 | 0.001258% | 0% | 0.0003755% | 0% | 1.439% | 0% | 0.4601% | 3.274% | 6.92% | 0.001246% | 0% | 0% | 0% | 0% | 12.1% | 19.4 | 0 | 6 | 0 | 0 | 0 | 0 | 51110.8 | 108020 | 19.444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 766.7 | 0 | 245.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 11 | 0 | 845 | 689.8 | 565.2 | 1735 | 107304 | 617950 | 8745.5 | 13606 | 67322 | 9023 | 159058 | 417798 | 6279
HighriseApartment | 2 - Prototype-NewHvacLoadsConstSch¦4b - Typical-Bar-Blend |  | Boise Air Terminal Uo | 222080 | 0.2 | 2.6327 | 16.25 | 8 | 15.75 | 7.25 | 224110 | 2020 | 0 | 0 | 0 | 16.086 | 0.001258% | 0% | 0.0003755% | 0% | 1.439% | 0% | 1.477% | 1.612% | 2.599% | 0.002135% | 0% | 0% | 0% | 0% | 7.13% | 19.4 | 0 | 6 | 0 | 0 | 0 | 0 | 25158 | 40578 | 33.333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 766.5 | 0 | 786.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177210.4 | 646750 | 0 | 194584.3 | 657.9 | 15413.5 | 89.3 | 410142 | 1050963 | 7746.7 | 341469 | 58358 | 38109 | 564976 | 732662 | 8487
HighriseApartment | 2 - Prototype-NewHvacLoadsConstSch¦4c - Typical-Urban-Blend |  | Boise Air Terminal Uo | 63590 | 58.9 | 0.7103 | 16 | 50.5 | 15.5 | 49.75 | 104080 | 40490 | 0 | 0 | 0 | 3.093 | 0.002121% | 0% | 0.01483% | 0% | 1.439% | 0% | 2.199% | 0.4756% | 1.464% | 0.002313% | 0% | 0% | 0% | 0% | 5.597% | 33.4 | 0 | 230 | 0 | 0 | 0 | 0 | 7425 | 22850 | 36.111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 766.6 | 0 | 1171.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 655 | 0 | 1264 | 144.2 | 1679.4 | 21.9 | 38089 | 26840 | 10788 | 20640 | 37376 | 18123 | 25983 | 5096 | 8511
HighriseApartment | 2 - Prototype-NewHvacLoadsConstSch¦4d - Prototype-Prototype-Blend |  | Boise Air Terminal Uo | 56610 | 0 | 0.6711 | 4.75 | 12.25 | 5.25 | 13 | 27230 | 29370 | 0 | 0 | 0 | 1.835 | 0% | 0% | 0% | 0% | 0.0003755% | 0% | 0.5518% | 0.006777% | 0.5039% | 0.0005338% | 0% | 0% | 0% | 0% | 1.063% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 7866 | 8.333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 293.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 203.2 | 1800.5 | 0.7 | 448 | 2670 | 347.5 | 26686 | 29183 | 1557 | 1497 | 3467 | 1497
chart | [19 empty] | big drop in internal gains for blended bar (why so different than other two blended methods?)
StripMall | 0 - Prototype | run/Prototype Row B/datapoint_59c942e553ff6b03c862017d | Boise Air Terminal Uo | 1874280 | 22500 | 83.3013 | 391.25 | 360 | 35.75 | 0 | 1310330 | 563951 | 0 | 0 | 0 | 127.028 | 605560 | 136116 | 122837 | 0 | 36642.6 | 0 | 563951 | 117861 | 291321 | 0 | 0 | 0 | 0 | 0 |  | 177472 | 39891.7 | 36000 | 0 | 10738.9 | 0 | 0 | 34541.7 | 85377.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5640.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 605558 | 122834 | 0 | 72951.8 | 53038.9 | 35286.9 | 73880.4 | 234714 | 188405 | 283360 | 263859 | 312698 | 205199 | 321856 | 89174.1 | 409114
StripMall | 1 - Prototype-NewHvac | run/Prototype Row B/datapoint_59c942ed53ff6b03c862018d | Boise Air Terminal Uo | 1764140 | 22500 | 78.4063 | 808.25 | 918.25 | 491.25 | 497.75 | 1262790 | 501348 | 0 | 0 | 0 | 130.798 | 605560 | 136116 | 122837 | 0 | 36623.7 | 0 | 503357 | 131728 | 227912 | 0 | 0 | 0 | 0 | 0 |  | 177472 | 39891.7 | 36000 | 0 | 10733.3 | 0 | 588.889 | 38605.6 | 66794.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5014.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 605558 | 122834 | 0 | 72050.7 | 53398 | 35199.3 | 68657.4 | 233907 | 187546 | 282204 | 269051 | 274760 | 225799 | 323713 | 90420.2 | 411593
StripMall | 2 - Prototype-NewHvacLoadsConstSch | run/Prototype Row B/datapoint_59c942f553ff6b03c862019d | Boise Air Terminal Uo | 1690620 | 22500 | 75.1387 | 992.25 | 808.75 | 537.75 | 512.25 | 1239440 | 451180 | 0 | 0 | 0 | 118.277 | 605560 | 179981 | 122837 | 0 | 86185 | 0 | 403448 | 122088 | 170531 | 0 | 0 | 0 | 0 | 0 |  | 177472 | 52747.2 | 36000 | 0 | 10608.3 | 0 | 661.111 | 35780.6 | 49977.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 499.975 | 0 | 4012.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 605558 | 122834 | 0 | 71724.6 | 51112 | 5918.66 | 47448.1 | 234667 | 188357 | 283873 | 93957.3 | 163354 | 309366 | 320968 | 88461.9 | 407586
StripMall | 3b - Typical-Bar-Sliced | run/Prototype Row B/datapoint_59c9430753ff6b03c86201ad | Boise Air Terminal Uo | 1759130 | 22497 | 78.194 | 1513 | 812 | 537.5 | 626.25 | 1231560 | 527574 | 0 | 0 | 0 | 112.196 | 605475 | 179972 | 122818 | 0 | 40614 | 0 | 489538 | 125226 | 195478 | 0 | 0 | 0 | 0 | 0 |  | 177447 | 52744.4 | 35994.4 | 0 | 0 | 0 | 758.333 | 36700 | 57288.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406.218 | 0 | 4870.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 605478 | 122818 | 0 | 71468.2 | 51001.8 | 5877.65 | 105131 | 242624 | 148063 | 272952 | 86900 | 213299 | 341534 | 324370 | 72806.2 | 391473
StripMall | 4b - Typical-Bar-Blend | run/Prototype Row B/datapoint_59c9431053ff6b03c86201bd | Boise Air Terminal Uo | 1643970 | 22497 | 73.0751 | 1172 | 477 | 423 | 444 | 1181480 | 462497 | 0 | 0 | 0 | 107.951 | 605475 | 179972 | 122818 | 0 | 40614 | 0 | 423769 | 115255 | 156077 | 0 | 0 | 0 | 0 | 0 |  | 177447 | 52744.4 | 35994.4 | 0 | 0 | 0 | 552.778 | 33777.8 | 45741.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406.218 | 0 | 4219.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 605478 | 122818 | 0 | 71791.1 | 51694.3 | 5896.08 | 108934 | 241831 | 148383 | 272585 | 88240.7 | 168661 | 343707 | 324860 | 72617.5 | 390668
StripMall | 4c - Typical-Urban-Blend | run/Prototype Row B/datapoint_59c9432b53ff6b03c86201cf | Boise Air Terminal Uo | 1811550 | 22501.1 | 80.5096 | 671 | 214 | 199.25 | 212.25 | 1311700 | 499850 | 0 | 0 | 0 | 114.941 | 605589 | 179972 | 122837 | 0 | 40614 | 0 | 461511 | 128088 | 272943 | 0 | 0 | 0 | 0 | 0 |  | 177481 | 52744.4 | 36000 | 0 | 0 | 0 | 669.444 | 37538.9 | 79991.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406.218 | 0 | 4593.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 605588 | 122840 | 0 | 71209.9 | 51962.6 | 5859.45 | 164238 | 182671 | 390712 | 260123 | 86279.6 | 253428 | 453148 | 252692 | 183970 | 383522
StripMall | 4d - Prototype-Prototype-Blend | run/Prototype Row B/datapoint_59c991be45b421004abe3ab0 | Boise Air Terminal Uo | 1639360 | 22500 | 72.8605 | 498.75 | 382 | 293 | 340 | 1235230 | 404130 | 0 | 0 | 0 | 118.503 | 605560 | 179981 | 122837 | 0 | 86185 | 0 | 355754 | 122221 | 166825 | 0 | 0 | 0 | 0 | 0 |  | 177472 | 52747.2 | 36000 | 0 | 10608.3 | 0 | 472.222 | 35819.4 | 48891.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 499.975 | 0 | 3542.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 605558 | 122834 | 0 | 71907.5 | 51847.5 | 5931.04 | 48383 | 234570 | 188339 | 283772 | 94069.8 | 139290 | 309531 | 319942 | 88182.6 | 407078
| bonus - 0 ot 2 error as single step | [15 empty] | 0 | 43865 | 0 | 0 | 49542.4 | 0 | 160503 | 4227 | 120790 | 0 | 0 | 0 | 0 | 0 | 20.22%
StripMall | 0 - Prototype¦1 - Prototype-NewHvac |  | Boise Air Terminal Uo | 110140 | 0 | 4.895 | 417 | 558.25 | 455.5 | 497.75 | 47540 | 62603 | 0 | 0 | 0 | 3.77 | 0% | 0% | 0% | 0% | 0.001008% | 0% | 3.233% | 0.7399% | 3.383% | 0% | 0% | 0% | 0% | 0% | 7.357% | 0 | 0 | 0 | 0 | 5.6 | 0 | 588.889 | 4063.9 | 18583.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 626.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 901.1 | 359.1 | 87.6 | 5223 | 807 | 859 | 1156 | 5192 | 37938 | 20600 | 1857 | 1246.1 | 2479
StripMall | 1 - Prototype-NewHvac¦2 - Prototype-NewHvacLoadsConstSch |  | Boise Air Terminal Uo | 73520 | 0 | 3.2676 | 184 | 109.5 | 46.5 | 14.5 | 23350 | 50168 | 0 | 0 | 0 | 12.521 | 0% | 2.486% | 0% | 0% | 2.809% | 0% | 5.663% | 0.5464% | 3.253% | 0% | 0% | 0% | 0% | 0% | 14.76% | 0 | 12855.5 | 0 | 0 | 125 | 0 | 72.222 | 2825 | 16816.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 499.975 | 0 | 1001.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326.1 | 2286 | 29280.64 | 21209.3 | 760 | 811 | 1669 | 175093.7 | 111406 | 83567 | 2745 | 1958.3 | 4007
StripMall | 2 - Prototype-NewHvacLoadsConstSch¦3b - Typical-Bar-Sliced |  | Boise Air Terminal Uo | 68510 | 3 | 3.0553 | 520.75 | 3.25 | 0.25 | 114 | 7880 | 76394 | 0 | 0 | 0 | 6.081 | 0.005028% | 0.0005323% | 0.001124% | 0% | 2.696% | 0% | 5.092% | 0.1856% | 1.476% | 0% | 0% | 0% | 0% | 0% | 9.456% | 25 | 2.8 | 5.6 | 0 | 10608.3 | 0 | 97.222 | 919.4 | 7311.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.757 | 0 | 857.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 16 | 0 | 256.4 | 110.2 | 41.01 | 57682.9 | 7957 | 40294 | 10921 | 7057.3 | 49945 | 32168 | 3402 | 15655.7 | 16113
StripMall | 2 - Prototype-NewHvacLoadsConstSch¦4b - Typical-Bar-Blend |  | Boise Air Terminal Uo | 46650 | 3 | 2.0636 | 179.75 | 331.75 | 114.75 | 68.25 | 57960 | 11317 | 0 | 0 | 0 | 10.326 | 0.005028% | 0.0005323% | 0.001124% | 0% | 2.696% | 0% | 1.202% | 0.4042% | 0.855% | 0% | 0% | 0% | 0% | 0% | 5.163% | 25 | 2.8 | 5.6 | 0 | 10608.3 | 0 | 108.333 | 2002.8 | 4236.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.757 | 0 | 206.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 16 | 0 | 66.5 | 582.3 | 22.58 | 61485.9 | 7164 | 39974 | 11288 | 5716.6 | 5307 | 34341 | 3892 | 15844.4 | 16918
StripMall | 2 - Prototype-NewHvacLoadsConstSch¦4c - Typical-Urban-Blend |  | Boise Air Terminal Uo | 120930 | 1.1 | 5.3709 | 321.25 | 594.75 | 338.5 | 300 | 72260 | 48670 | 0 | 0 | 0 | 3.336 | 0.001715% | 0.0005323% | 0% | 0% | 2.696% | 0% | 3.434% | 0.3549% | 6.058% | 0% | 0% | 0% | 0% | 0% | 12.54% | 9 | 2.8 | 0 | 0 | 10608.3 | 0 | 8.333 | 1758.3 | 30013.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.757 | 0 | 580.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 6 | 0 | 514.7 | 850.6 | 59.21 | 116789.9 | 51996 | 202355 | 23750 | 7677.7 | 90074 | 143782 | 68276 | 95508.1 | 24064
StripMall | 2 - Prototype-NewHvacLoadsConstSch¦4d - Prototype-Prototype-Blend |  | Boise Air Terminal Uo | 51260 | 0 | 2.2782 | 493.5 | 426.75 | 244.75 | 172.25 | 4210 | 47050 | 0 | 0 | 0 | 0.226 | 0% | 0% | 0% | 0% | 0% | 0% | 2.821% | 0.007867% | 0.2192% | 0% | 0% | 0% | 0% | 0% | 3.048% | 0 | 0 | 0 | 0 | 0 | 0 | 188.889 | 38.8 | 1086.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182.9 | 735.5 | 12.38 | 934.9 | 97 | 18 | 101 | 112.5 | 24064 | 165 | 1026 | 279.3 | 508
chart | [19 empty] | why bigger window gain on typical blend urban
Retail | 0 - Prototype | run/Prototype Row B/datapoint_59c942e553ff6b03c862017e | Boise Air Terminal Uo | 1856860 | 24692.3 | 75.1999 | 147.25 | 470 | 0 | 0 | 1361860 | 494988 | 0 | 0 | 0 | 114.691 | 470942 | 108885 | 187308 | 0 | 55599 | 0 | 439389 | 121709 | 473027 | 0 | 0 | 0 | 0 | 0 |  | 138019 | 31911.1 | 54894.4 | 0 | 0 | 0 | 0 | 35669.4 | 138631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 556.097 | 0 | 4394.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470940 | 187303 | 0 | 230441 | 34759.8 | 1894.3 | 46440.3 | 434117 | 154897 | 325203 | 183490 | 180146 | 230424 | 555447 | 59363.4 | 465701
Retail | 1 - Prototype-NewHvac | run/Prototype Row B/datapoint_59c942ed53ff6b03c862018e | Boise Air Terminal Uo | 1915790 | 24692.3 | 77.5867 | 449.5 | 656.25 | 132 | 83 | 1359890 | 555904 | 0 | 0 | 0 | 125.379 | 470942 | 108885 | 187308 | 0 | 55599 | 0 | 502874 | 147803 | 442394 | 0 | 0 | 0 | 0 | 0 |  | 138019 | 31911.1 | 54894.4 | 0 | 0 | 0 | 752.778 | 43316.7 | 129653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 556.097 | 0 | 5004.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470940 | 187303 | 0 | 228225 | 38887.6 | 1636.7 | 44618.7 | 433078 | 153989 | 324408 | 202921 | 188521 | 246761 | 557420 | 60750.5 | 467496
Retail | 2 - Prototype-NewHvacLoadsConstSch | run/Prototype Row B/datapoint_59c942f553ff6b03c862019e | Boise Air Terminal Uo | 1783480 | 24692.3 | 72.2281 | 491.75 | 495.75 | 145.25 | 73.5 | 1206990 | 576491 | 0 | 0 | 0 | 115.982 | 470942 | 114970 | 187308 | 0 | 55599 | 0 | 523347 | 126391 | 304922 | 0 | 0 | 0 | 0 | 0 |  | 138019 | 33694.4 | 54894.4 | 0 | 0 | 0 | 719.444 | 37041.7 | 89363.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 556.097 | 0 | 5209.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470940 | 187303 | 0 | 229775 | 38449.5 | 6033.71 | 26945.1 | 435488 | 155007 | 326947 | 100052 | 240565 | 336036 | 551703 | 58507.3 | 460926
Retail | 3b - Typical-Bar-Sliced | run/Prototype Row B/datapoint_59c9430753ff6b03c86201ae | Boise Air Terminal Uo | 1779690 | 24692 | 72.0755 | 1052.25 | 490 | 229.5 | 73 | 1183620 | 596063 | 0 | 0 | 0 | 115.965 | 470942 | 114970 | 187270 | 0 | 0 | 0 | 599191 | 134543 | 272763 | 0 | 0 | 0 | 0 | 0 |  | 138019 | 33694.4 | 54883.3 | 0 | 0 | 0 | 916.667 | 39430.6 | 79938.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5961.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470938 | 187273 | 0 | 229812 | 37823.2 | 6145.45 | 64926.4 | 442365 | 100533 | 294333 | 95591.7 | 260945 | 348876 | 551150 | 48642.5 | 430918
Retail | 4b - Typical-Bar-Blend | run/Prototype Row B/datapoint_59c9431053ff6b03c86201be | Boise Air Terminal Uo | 1726710 | 24692 | 69.9302 | 1016 | 404 | 204.25 | 58.75 | 1150890 | 575827 | 0 | 0 | 0 | 110.447 | 470942 | 114970 | 187270 | 0 | 0 | 0 | 578434 | 120866 | 254233 | 0 | 0 | 0 | 0 | 0 |  | 138019 | 33694.4 | 54883.3 | 0 | 0 | 0 | 763.889 | 35422.2 | 74508.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5759.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470938 | 187273 | 0 | 230126 | 37735.8 | 6156.88 | 79904.7 | 441158 | 100770 | 293284 | 96502.5 | 265565 | 352120 | 551021 | 47764 | 427861
Retail | 4c - Typical-Urban-Blend | run/Prototype Row B/datapoint_59c9432b53ff6b03c86201d0 | Boise Air Terminal Uo | 1862400 | 24686.4 | 75.4426 | 606.75 | 71.5 | 94 | 26.5 | 1265930 | 596471 | 0 | 0 | 0 | 117.795 | 470828 | 114970 | 187232 | 0 | 0 | 0 | 600262 | 142419 | 346693 | 0 | 0 | 0 | 0 | 0 |  | 137986 | 33694.4 | 54872.2 | 0 | 0 | 0 | 1111.11 | 41738.9 | 101606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5965.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470832 | 187231 | 0 | 227750 | 37798 | 6151.55 | 136860 | 324927 | 413228 | 280238 | 94953.7 | 341376 | 474452 | 414289 | 188748 | 421076
Retail | 4d - Prototype-Prototype-Blend | run/Prototype Row B/datapoint_59c991be45b421004abe3ab1 | Boise Air Terminal Uo | 1782580 | 24692.3 | 72.1917 | 386 | 405 | 126.25 | 56.5 | 1209620 | 572946 | 0 | 0 | 0 | 116.527 | 470942 | 114970 | 187308 | 0 | 55599 | 0 | 519546 | 127510 | 306704 | 0 | 0 | 0 | 0 | 0 |  | 138019 | 33694.4 | 54894.4 | 0 | 0 | 0 | 644.444 | 37369.4 | 89886.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 556.097 | 0 | 5174.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470940 | 187303 | 0 | 229872 | 38544.1 | 6152.2 | 28766.8 | 435436 | 155533 | 327075 | 100358 | 253909 | 336898 | 551290 | 58117.4 | 460318
| bonus - 0 ot 2 error as single step | [15 empty] | 0 | 6085 | 0 | 0 | 0 | 0 | 83958 | 4682 | 168105 | 0 | 0 | 0 | 0 | 0 | 14.15%
Retail | 0 - Prototype¦1 - Prototype-NewHvac |  | Boise Air Terminal Uo | 58930 | 0 | 2.3868 | 302.25 | 186.25 | 132 | 83 | 1970 | 60916 | 0 | 0 | 0 | 10.688 | 0% | 0% | 0% | 0% | 0% | 0% | 3.419% | 1.405% | 1.65% | 0% | 0% | 0% | 0% | 0% | 6.474% | 0 | 0 | 0 | 0 | 0 | 0 | 752.778 | 7647.3 | 8978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 609.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2216 | 4127.8 | 257.6 | 1821.6 | 1039 | 908 | 795 | 19431 | 8375 | 16337 | 1973 | 1387.1 | 1795
Retail | 1 - Prototype-NewHvac¦2 - Prototype-NewHvacLoadsConstSch |  | Boise Air Terminal Uo | 132310 | 0 | 5.3586 | 42.25 | 160.5 | 13.25 | 9.5 | 152900 | 20587 | 0 | 0 | 0 | 9.397 | 0% | 0.3176% | 0% | 0% | 0% | 0% | 1.069% | 1.118% | 7.176% | 0% | 0% | 0% | 0% | 0% | 9.68% | 0 | 1783.3 | 0 | 0 | 0 | 0 | 33.334 | 6275 | 40289.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1550 | 438.1 | 4397.01 | 17673.6 | 2410 | 1018 | 2539 | 102869 | 52044 | 89275 | 5717 | 2243.2 | 6570
Retail | 2 - Prototype-NewHvacLoadsConstSch¦3b - Typical-Bar-Sliced |  | Boise Air Terminal Uo | 3790 | 0.3 | 0.1526 | 560.5 | 5.75 | 84.25 | 0.5 | 23370 | 19572 | 0 | 0 | 0 | 0.017 | 0% | 0% | 0.002131% | 0% | 3.117% | 0% | 4.253% | 0.4571% | 1.803% | 0% | 0% | 0% | 0% | 0% | 9.632% | 0 | 0 | 11.1 | 0 | 0 | 0 | 197.223 | 2388.9 | 9425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 556.097 | 0 | 751.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 30 | 0 | 37 | 626.3 | 111.74 | 37981.3 | 6877 | 54474 | 32614 | 4460.3 | 20380 | 12840 | 553 | 9864.8 | 30008
Retail | 2 - Prototype-NewHvacLoadsConstSch¦4b - Typical-Bar-Blend |  | Boise Air Terminal Uo | 56770 | 0.3 | 2.2979 | 524.25 | 91.75 | 59 | 14.75 | 56100 | 664 | 0 | 0 | 0 | 5.535 | 0% | 0% | 0.002131% | 0% | 3.117% | 0% | 3.089% | 0.3098% | 2.842% | 0% | 0% | 0% | 0% | 0% | 9.36% | 0 | 0 | 11.1 | 0 | 0 | 0 | 44.445 | 1619.5 | 14855.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 556.097 | 0 | 549.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 30 | 0 | 351 | 713.7 | 123.17 | 52959.6 | 5670 | 54237 | 33663 | 3549.5 | 25000 | 16084 | 682 | 10743.3 | 33065
Retail | 2 - Prototype-NewHvacLoadsConstSch¦4c - Typical-Urban-Blend |  | Boise Air Terminal Uo | 78920 | 5.9 | 3.2145 | 115 | 424.25 | 51.25 | 47 | 58940 | 19980 | 0 | 0 | 0 | 1.813 | 0.006392% | 0% | 0.004261% | 0% | 3.117% | 0% | 4.313% | 0.8987% | 2.342% | 0% | 0% | 0% | 0% | 0% | 10.68% | 33 | 0 | 22.2 | 0 | 0 | 0 | 391.666 | 4697.2 | 12242.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 556.097 | 0 | 755.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 72 | 0 | 2025 | 651.5 | 117.84 | 109914.9 | 110561 | 258221 | 46709 | 5098.3 | 100811 | 138416 | 137414 | 130240.7 | 39850
Retail | 2 - Prototype-NewHvacLoadsConstSch¦4d - Prototype-Prototype-Blend |  | Boise Air Terminal Uo | 900 | 0 | 0.0364 | 105.75 | 90.75 | 19 | 17 | 2630 | 3545 | 0 | 0 | 0 | 0.545 | 0% | 0% | 0% | 0% | 0% | 0% | 0.2131% | 0.06274% | 0.09992% | 0% | 0% | 0% | 0% | 0% | 0.3758% | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 327.7 | 522.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 94.6 | 118.49 | 1821.7 | 52 | 526 | 128 | 306 | 13344 | 862 | 413 | 389.9 | 608
chart | [19 empty] | why bigger window gain on typical blend urban
Hospital | 0 - Prototype | run/Prototype Row B/datapoint_59c942e553ff6b03c8620177 | Boise Air Terminal Uo | 34685900 | 241501 | 143.626 | 1813.25 | 36 | 267.5 | 36 | 23176900 | 11508900 | 0 | 0 | 0 | 1329.96 | 3795000 | 2669380 | 9983920 | 0 | 1232830 | 110345 | 7701540 | 2090840 | 4117220 | 653169 | 332409 | 1999240 | 0 | 0 |  | 1112210 | 782319 | 2170860 | 0 | 594.444 | 32338.9 | 0 | 612764 | 1206640 | 191425 | 97419.4 | 585919 | 0 | 0 | 0 | 0 | 25771.2 | 0 | 12310.3 | 0 | 77030.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3364730 | 6408180 | 2576620 | 517922 | 357833 | 8177.22 | 773.7 | 1141130 | 521864 | 455086 | 98977.7 | 1827320 | 548746 | 1493850 | 266360 | 679013
Hospital | 1 - Prototype-NewHvac | run/Prototype Row B/datapoint_59c942ed53ff6b03c8620187 | Boise Air Terminal Uo | 29745900 | 241501 | 123.171 | 794.75 | 2010.75 | 520.75 | 1192.5 | 21468600 | 8277310 | 0 | 0 | 0 | 1280.56 | 3795000 | 2669380 | 9983920 | 0 | 1232840 | 118202 | 4469880 | 3739550 | 3165100 | 472790 | 99227 | 0 | 0 | 0 |  | 1112210 | 782319 | 2170860 | 0 | 594.444 | 34641.7 | 0 | 1095950 | 927600 | 138561 | 29080.6 | 0 | 0 | 0 | 0 | 0 | 25771.2 | 0 | 12310.4 | 0 | 44707.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3364730 | 6408180 | 2576620 | 500654 | 285060 | 7017.7 | 348.4 | 1128660 | 520100 | 439079 | 104465 | 174227 | 755913 | 1520800 | 266812 | 722982
Hospital | 2 - Prototype-NewHvacLoadsConstSch | run/Prototype Row B/datapoint_59c942f553ff6b03c8620197 | Boise Air Terminal Uo | 29502800 | 241501 | 122.164 | 926.25 | 2052.75 | 659.5 | 1167.25 | 20901000 | 8601730 | 0 | 0 | 0 | 1227.14 | 3795000 | 462269 | 11478000 | 0 | 783740 | 118193 | 5243400 | 3812040 | 3225930 | 483320 | 100848 | 0 | 0 | 0 |  | 1112210 | 135478 | 2608740 | 0 | 594.444 | 34638.9 | 0 | 1117200 | 945428 | 141647 | 29555.6 | 0 | 0 | 0 | 0 | 0 | 25771.2 | 0 | 7818.63 | 0 | 52444.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3364730 | 6408800 | 2576620 | 501954 | 266016 | 28055.2 | 348.3 | 1126220 | 520952 | 439810 | 414723 | 435803 | 756050 | 1525510 | 265244 | 721214
Hospital | 3b - Typical-Bar-Sliced | run/Prototype Row B/datapoint_59c9430753ff6b03c86201a7 | Boise Air Terminal Uo | 29893100 | 241501 | 123.78 | 1111 | 2464 | 560.75 | 1642 | 21385000 | 8508120 | 0 | 0 | 0 | 1307.7 | 3920040 | 455777 | 12483200 | 0 | 808128 | 0 | 4608500 | 3856670 | 3210620 | 468572 | 81607.1 | 0 | 0 | 0 |  | 1148850 | 133575 | 2752440 | 0 | 0 | 0 | 0 | 1130280 | 940939 | 137325 | 23916.7 | 0 | 0 | 0 | 0 | 0 | 30920.9 | 0 | 8082.84 | 0 | 46093.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3920040 | 7840280 | 3091500 | 726123 | 370245 | 39181 | 428.9 | 1696940 | 966445 | 401545 | 668539 | 300020 | 1438150 | 2387430 | 604871 | 726262
Hospital | 4b - Typical-Bar-Blend | run/Prototype Row B/datapoint_59c9431053ff6b03c86201b7 | Boise Air Terminal Uo | 25422200 | 241501 | 105.267 | 363 | 1078 | 363 | 1078 | 19438100 | 5984070 | 0 | 0 | 0 | 1247.21 | 3920040 | 455777 | 12483200 | 0 | 808128 | 0 | 2084450 | 3211740 | 1691750 | 639407 | 127718 | 0 | 0 | 0 |  | 1148850 | 133575 | 2752440 | 0 | 0 | 0 | 0 | 941267 | 495803 | 187392 | 37430.6 | 0 | 0 | 0 | 0 | 0 | 30920.9 | 0 | 8082.84 | 0 | 20848.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2613360 | 5226850 | 2061000 | 462300 | 361149 | 24507.8 | 311.9 | 862823 | 487489 | 409430 | 434874 | 126363 | 1536240 | 1203010 | 297817 | 770120
Hospital | 4c - Typical-Urban-Blend | run/Prototype Row B/datapoint_59c9432b53ff6b03c86201c9 | Boise Air Terminal Uo | 23904700 | 241496 | 98.9862 | 318.25 | 1737 | 318.25 | 1737 | 18271300 | 5633410 | 0 | 0 | 0 | 1203.55 | 3919950 | 455777 | 12482900 | 0 | 808128 | 0 | 1733860 | 3043390 | 670287 | 663993 | 126410 | 0 | 0 | 0 |  | 1148830 | 133575 | 2752375 | 0 | 0 | 0 | 0 | 891931 | 196442 | 194597 | 37047.2 | 0 | 0 | 0 | 0 | 0 | 30920.3 | 0 | 8082.84 | 0 | 17342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3919950 | 7840100 | 3091430 | 686284 | 313127 | 49906.3 | 362.9 | 1620390 | 2077020 | 365531 | 939170 | 93594.6 | 1641640 | 2532360 | 1500420 | 749729
Hospital | 4d - Prototype-Prototype-Blend | run/Prototype Row B/datapoint_59c991be45b421004abe3aaa | Boise Air Terminal Uo | 24778200 | 241501 | 102.601 | 618.75 | 1317 | 618.75 | 1317 | 18594900 | 6183330 | 0 | 0 | 0 | 1191.84 | 3795000 | 462269 | 11478000 | 0 | 783740 | 114705 | 2825000 | 3063490 | 1504510 | 635066 | 116430 | 0 | 0 | 0 |  | 1112210 | 135478 | 2608740 | 0 | 594.444 | 33616.7 | 0 | 897819 | 440928 | 186119 | 34122.2 | 0 | 0 | 0 | 0 | 0 | 25771.2 | 0 | 7818.63 | 0 | 28255.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3364350 | 6567250 | 2284230 | 595294 | 386294 | 33382.6 | 169 | 1116010 | 508013 | 446816 | 591431 | 292761 | 1173380 | 1535860 | 279304 | 695284
| bonus - 0 ot 2 error as single step | [15 empty] | 0 | 2207111 | 1494080 | 0 | 449090 | 7848 | 2458140 | 1721200 | 891290 | 169849 | 231561 | 1999240 | 0 | 0 | 33.53%
Hospital | 0 - Prototype¦1 - Prototype-NewHvac |  | Boise Air Terminal Uo | 4940000 | 0 | 20.455 | 1018.5 | 1974.75 | 253.25 | 1156.5 | 1708300 | 3231590 | 0 | 0 | 0 | 49.4 | 0% | 0% | 0% | 0% | 2.883e-07 | 0.02265% | 9.317% | 4.753% | 2.745% | 0.52% | 0.6723% | 5.764% | 0% | 0% | 23.79% | 0 | 0 | 0 | 0 | 0 | 2302.8 | 0 | 483186 | 279040 | 52864 | 68338.8 | 585919 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 32322.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17268 | 72773 | 1159.52 | 425.3 | 12470 | 1764 | 16007 | 5487.3 | 1653093 | 207167 | 26950 | 452 | 43969
Hospital | 1 - Prototype-NewHvac¦2 - Prototype-NewHvacLoadsConstSch |  | Boise Air Terminal Uo | 243100 | 0 | 1.007 | 131.5 | 42 | 138.75 | 25.25 | 567600 | 324420 | 0 | 0 | 0 | 53.42 | 0% | 7.42% | 5.023% | 0% | 1.51% | 3.0256e-07 | 2.6% | 0.2437% | 0.2045% | 0.0354% | 0.005449% | 0% | 0% | 0% | 17.04% | 0 | 646841 | 437880 | 0 | 0 | 2.8 | 0 | 21250 | 17828 | 3086 | 475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4491.77 | 0 | 7736.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 620 | 0 | 1300 | 19044 | 21037.5 | 0.1 | 2440 | 852 | 731 | 310258 | 261576 | 137 | 4710 | 1568 | 1768
Hospital | 2 - Prototype-NewHvacLoadsConstSch¦3b - Typical-Bar-Sliced |  | Boise Air Terminal Uo | 390300 | 0 | 1.616 | 184.75 | 411.25 | 98.75 | 474.75 | 484000 | 93610 | 0 | 0 | 0 | 80.56 | 0.4238% | 0.022% | 3.407% | 0% | 0.08266% | 0.4006% | 2.152% | 0.1513% | 0.05189% | 0.04999% | 0.06522% | 0% | 0% | 0% | 6.807% | 36640 | 1903 | 143700 | 0 | 594.444 | 34638.9 | 0 | 13080 | 4489 | 4322 | 5638.9 | 0 | 0 | 0 | 0 | 0 | 5149.7 | 0 | 264.21 | 0 | 6350.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555310 | 1431480 | 514880 | 224169 | 104229 | 11125.8 | 80.6 | 570720 | 445493 | 38265 | 253816 | 135783 | 682100 | 861920 | 339627 | 5048
Hospital | 2 - Prototype-NewHvacLoadsConstSch¦4b - Typical-Bar-Blend |  | Boise Air Terminal Uo | 4080600 | 0 | 16.897 | 563.25 | 974.75 | 296.5 | 89.25 | 1462900 | 2617660 | 0 | 0 | 0 | 20.07 | 0.4238% | 0.022% | 3.407% | 0% | 0.08266% | 0.4006% | 10.71% | 2.035% | 5.2% | 0.5291% | 0.09108% | 0% | 0% | 0% | 22.9% | 36640 | 1903 | 143700 | 0 | 594.444 | 34638.9 | 0 | 175933 | 449625 | 45745 | 7875 | 0 | 0 | 0 | 0 | 0 | 5149.7 | 0 | 264.21 | 0 | 31595.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 751370 | 1181950 | 515620 | 39654 | 95133 | 3547.4 | 36.4 | 263397 | 33463 | 30380 | 20151 | 309440 | 780190 | 322500 | 32573 | 48906
Hospital | 2 - Prototype-NewHvacLoadsConstSch¦4c - Typical-Urban-Blend |  | Boise Air Terminal Uo | 5598100 | 5 | 23.1778 | 608 | 315.75 | 341.25 | 569.75 | 2629700 | 2968320 | 0 | 0 | 0 | 23.59 | 0.4235% | 0.022% | 3.406% | 0% | 0.08266% | 0.4006% | 11.9% | 2.605% | 8.662% | 0.6124% | 0.08664% | 0% | 0% | 0% | 28.2% | 36620 | 1903 | 143635 | 0 | 594.444 | 34638.9 | 0 | 225269 | 748986 | 52950 | 7491.6 | 0 | 0 | 0 | 0 | 0 | 5149.1 | 0 | 264.21 | 0 | 35102.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555220 | 1431300 | 514810 | 184330 | 47111 | 21851.1 | 14.6 | 494170 | 1556068 | 74279 | 524447 | 342208.4 | 885590 | 1006850 | 1235176 | 28515
Hospital | 2 - Prototype-NewHvacLoadsConstSch¦4d - Prototype-Prototype-Blend |  | Boise Air Terminal Uo | 4724600 | 0 | 19.563 | 307.5 | 735.75 | 40.75 | 149.75 | 2306100 | 2418400 | 0 | 0 | 0 | 35.3 | 0% | 0% | 0% | 0% | 0% | 0.01182% | 8.197% | 2.537% | 5.835% | 0.5143% | 0.05282% | 0% | 0% | 0% | 17.15% | 0 | 0 | 0 | 0 | 0 | 1022.2 | 0 | 219381 | 504500 | 44472 | 4566.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24188.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 158450 | 292390 | 93340 | 120278 | 5327.4 | 179.3 | 10210 | 12939 | 7006 | 176708 | 143042 | 417330 | 10350 | 14060 | 25930
chart | [19 empty] | big drop in ventilation when add new hvac, why do plug loads change when sliced
Outpatient | 0 - Prototype | run/Prototype Row B/datapoint_59c942e553ff6b03c862017b | Boise Air Terminal Uo | 6491030 | 40946 | 158.527 | 6220.25 | 894 | 4986.75 | 257.25 | 5428370 | 1062660 | 0 | 0 | 0 | 333.084 | 593997 | 214766 | 1967840 | 0 | 128372 | 0 | 1645370 | 669898 | 1064860 | 19894.7 | 0 | 186028 | 0 | 0 |  | 174083 | 62941.7 | 523778 | 0 | 0 | 0 | 261336 | 196328 | 312081 | 5830.56 | 0 | 54519.4 | 0 | 0 | 0 | 0 | 1806.7 | 0 | 1283.97 | 0 | 7538.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 593995 | 1165370 | 90316.8 | 419291 | 151879 | 6369.79 | 49964.4 | 289249 | 372894 | 171032 | 48071.4 | 362861 | 75344.2 | 376871 | 172440 | 246078
Outpatient | 1 - Prototype-NewHvac | run/Prototype Row B/datapoint_59c942ed53ff6b03c862018b | Boise Air Terminal Uo | 5019950 | 40946 | 122.599 | 2819 | 5165.75 | 204.5 | 2614.25 | 4046620 | 973332 | 0 | 0 | 0 | 312.049 | 593997 | 214766 | 1967840 | 0 | 128382 | 0 | 675803 | 543583 | 895517 | 75.8254 | 0 | 0 | 0 | 0 |  | 174083 | 62941.7 | 523778 | 0 | 0 | 0 | 3363.89 | 159308 | 262450 | 22.2222 | 0 | 0 | 0 | 0 | 0 | 0 | 1806.7 | 0 | 1284.07 | 0 | 6644.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 593995 | 1165370 | 90316.8 | 399330 | 142150 | 5513.55 | 12897.2 | 284454 | 360847 | 166503 | 60977.7 | 86357.5 | 151522 | 392748 | 194624 | 259662
Outpatient | 2 - Prototype-NewHvacLoadsConstSch | run/Prototype Row B/datapoint_59c942f553ff6b03c862019b | Boise Air Terminal Uo | 4863750 | 40946 | 118.784 | 1455.75 | 5404.75 | 307.75 | 2493 | 3908150 | 955599 | 0 | 0 | 0 | 301.037 | 592187 | 237637 | 1862680 | 0 | 162977 | 0 | 618091 | 533934 | 856173 | 75.8254 | 0 | 0 | 0 | 0 |  | 173553 | 69644.4 | 492958 | 0 | 0 | 0 | 1788.89 | 156481 | 250919 | 22.2222 | 0 | 0 | 0 | 0 | 0 | 0 | 1806.7 | 0 | 1630.09 | 0 | 6121.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 592184 | 1128650 | 90316.8 | 399435 | 126769 | 11548.7 | 8053 | 285858 | 361341 | 166637 | 131868 | 127171 | 164828 | 389724 | 192446 | 258510
Outpatient | 3b - Typical-Bar-Sliced | run/Prototype Row B/datapoint_59c9430753ff6b03c86201ab | Boise Air Terminal Uo | 5058270 | 40946 | 123.535 | 1634.5 | 4875 | 377.5 | 2076.5 | 3955160 | 1103120 | 0 | 0 | 0 | 309.051 | 600253 | 233561 | 1907750 | 0 | 125728 | 0 | 783153 | 543839 | 863907 | 85.3035 | 0 | 0 | 0 | 0 |  | 175917 | 68450 | 501314 | 0 | 0 | 0 | 866.667 | 159383 | 253186 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 1972.31 | 0 | 1257.52 | 0 | 7803.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600253 | 1204500 | 98596.2 | 436566 | 137756 | 12436.9 | 4117.8 | 292182 | 359516 | 154202 | 140339 | 131882 | 213474 | 407837 | 199445 | 238428
Outpatient | 4b - Typical-Bar-Blend | run/Prototype Row B/datapoint_59c9431053ff6b03c86201bb | Boise Air Terminal Uo | 4344250 | 40946 | 106.097 | 859.25 | 2188.25 | 596.5 | 1674.5 | 3677870 | 666382 | 0 | 0 | 0 | 284.55 | 600253 | 233561 | 1907750 | 0 | 125700 | 0 | 343489 | 446185 | 687243 | 85.3035 | 0 | 0 | 0 | 0 |  | 175917 | 68450 | 501314 | 0 | 0 | 0 | 0 | 130764 | 201411 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 1972.31 | 0 | 1257.24 | 0 | 3435.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600253 | 1204500 | 98596.2 | 430296 | 106997 | 13454.6 | 1306.1 | 288784 | 356287 | 151021 | 157641 | 77027.9 | 261568 | 414217 | 206232 | 243196
Outpatient | 4c - Typical-Urban-Blend | run/Prototype Row B/datapoint_59c9432b53ff6b03c86201cd | Boise Air Terminal Uo | 4992480 | 44345.2 | 112.582 | 476.5 | 994.25 | 346 | 763.5 | 4440370 | 552113 | 0 | 0 | 0 | 330.254 | 650079 | 233561 | 2066120 | 0 | 125700 | 0 | 212851 | 587580 | 1116500 | 85.3035 | 0 | 0 | 0 | 0 |  | 190519 | 68450 | 542931 | 0 | 0 | 0 | 0 | 172203 | 327214 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 2136.03 | 0 | 1257.24 | 0 | 2128.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 650084 | 1304490 | 106781 | 463396 | 95092.9 | 14250.3 | 7352.3 | 251590 | 527788 | 157819 | 167670 | 79842.4 | 289680 | 374118 | 309237 | 261416
Outpatient | 4d - Prototype-Prototype-Blend | run/Prototype Row B/datapoint_59c991be45b421004abe3aae | Boise Air Terminal Uo | 4787220 | 40946 | 116.915 | 797 | 1870.5 | 541 | 1511 | 3818130 | 969086 | 0 | 0 | 0 | 297.723 | 592187 | 237637 | 1862680 | 0 | 162930 | 0 | 626289 | 470278 | 835150 | 75.8254 | 0 | 0 | 0 | 0 |  | 173553 | 69644.4 | 492958 | 0 | 0 | 0 | 225 | 137825 | 244758 | 22.2222 | 0 | 0 | 0 | 0 | 0 | 0 | 1806.7 | 0 | 1629.61 | 0 | 6256.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 592184 | 1128650 | 90316.8 | 395284 | 119111 | 12382 | 9775.8 | 285142 | 359801 | 165821 | 143444 | 156558 | 156386 | 389406 | 192101 | 258404
| bonus - 0 ot 2 error as single step | [15 empty] | 1810 | 22871 | 105160 | 0 | 34605 | 0 | 1027279 | 135964 | 208687 | 19818.8746 | 0 | 186028 | 0 | 0 | 26.84%
Outpatient | 0 - Prototype¦1 - Prototype-NewHvac |  | Boise Air Terminal Uo | 1471080 | 0 | 35.928 | 3401.25 | 4271.75 | 4782.25 | 2357 | 1381750 | 89328 | 0 | 0 | 0 | 21.035 | 0% | 0% | 0% | 0% | 0.0001541% | 0% | 14.94% | 1.946% | 2.609% | 0.3053% | 0% | 2.866% | 0% | 0% | 22.66% | 0 | 0 | 0 | 0 | 0 | 0 | 257972.11 | 37020 | 49631 | 5808.3378 | 0 | 54519.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 893.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19961 | 9729 | 856.24 | 37067.2 | 4795 | 12047 | 4529 | 12906.3 | 276503.5 | 76177.8 | 15877 | 22184 | 13584
Outpatient | 1 - Prototype-NewHvac¦2 - Prototype-NewHvacLoadsConstSch |  | Boise Air Terminal Uo | 156200 | 0 | 3.815 | 1363.25 | 239 | 103.25 | 121.25 | 138470 | 17733 | 0 | 0 | 0 | 11.012 | 0.03606% | 0.4556% | 2.095% | 0% | 0.6892% | 0% | 1.15% | 0.1922% | 0.7838% | 0% | 0% | 0% | 0% | 0% | 5.401% | 530 | 6702.7 | 30820 | 0 | 0 | 0 | 1575 | 2827 | 11531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346.02 | 0 | 523.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1811 | 36720 | 0 | 105 | 15381 | 6035.15 | 4844.2 | 1404 | 494 | 134 | 70890.3 | 40813.5 | 13306 | 3024 | 2178 | 1152
Outpatient | 2 - Prototype-NewHvacLoadsConstSch¦3b - Typical-Bar-Sliced |  | Boise Air Terminal Uo | 194520 | 0 | 4.751 | 178.75 | 529.75 | 69.75 | 416.5 | 47010 | 147521 | 0 | 0 | 0 | 8.014 | 0.1658% | 0.0838% | 0.9267% | 0% | 0.7658% | 0% | 3.394% | 0.2036% | 0.159% | 0.0001949% | 0% | 0% | 0% | 0% | 5.699% | 2364 | 1194.4 | 8356 | 0 | 0 | 0 | 922.223 | 2902 | 2267 | 2.7778 | 0 | 0 | 0 | 0 | 0 | 0 | 165.61 | 0 | 372.57 | 0 | 1682.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8069 | 75850 | 8279.4 | 37131 | 10987 | 888.2 | 3935.2 | 6324 | 1825 | 12435 | 8471 | 4711 | 48646 | 18113 | 6999 | 20082
Outpatient | 2 - Prototype-NewHvacLoadsConstSch¦4b - Typical-Bar-Blend |  | Boise Air Terminal Uo | 519500 | 0 | 12.687 | 596.5 | 3216.5 | 288.75 | 818.5 | 230280 | 289217 | 0 | 0 | 0 | 16.487 | 0.1658% | 0.0838% | 0.9267% | 0% | 0.7664% | 0% | 5.646% | 1.804% | 3.473% | 0.0001949% | 0% | 0% | 0% | 0% | 12.87% | 2364 | 1194.4 | 8356 | 0 | 0 | 0 | 1788.89 | 25717 | 49508 | 2.7778 | 0 | 0 | 0 | 0 | 0 | 0 | 165.61 | 0 | 372.85 | 0 | 2685.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8069 | 75850 | 8279.4 | 30861 | 19772 | 1905.9 | 6746.9 | 2926 | 5054 | 15616 | 25773 | 50143.1 | 96740 | 24493 | 13786 | 15314
Outpatient | 2 - Prototype-NewHvacLoadsConstSch¦4c - Typical-Urban-Blend |  | Boise Air Terminal Uo | 128730 | 3399.2 | 6.202 | 979.25 | 4410.5 | 38.25 | 1729.5 | 532220 | 403486 | 0 | 0 | 0 | 29.217 | 1.19% | 0.0838% | 4.183% | 0% | 0.7664% | 0% | 8.332% | 1.103% | 5.352% | 0.0001949% | 0% | 0% | 0% | 0% | 21.01% | 16966 | 1194.4 | 49973 | 0 | 0 | 0 | 1788.89 | 15722 | 76295 | 2.7778 | 0 | 0 | 0 | 0 | 0 | 0 | 329.33 | 0 | 372.85 | 0 | 3992.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57900 | 175840 | 16464.2 | 63961 | 31676.1 | 2701.6 | 700.7 | 34268 | 166447 | 8818 | 35802 | 47328.6 | 124852 | 15606 | 116791 | 2906
Outpatient | 2 - Prototype-NewHvacLoadsConstSch¦4d - Prototype-Prototype-Blend |  | Boise Air Terminal Uo | 76530 | 0 | 1.869 | 658.75 | 3534.25 | 233.25 | 982 | 90020 | 13487 | 0 | 0 | 0 | 3.314 | 0% | 0% | 0% | 0% | 0.0009663% | 0% | 0.1686% | 1.309% | 0.4322% | 0% | 0% | 0% | 0% | 0% | 1.911% | 0 | 0 | 0 | 0 | 0 | 0 | 1563.89 | 18656 | 6161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.48 | 0 | 135.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4151 | 7658 | 833.3 | 1722.8 | 716 | 1540 | 816 | 11576 | 29387 | 8442 | 318 | 345 | 106
chart | [19 empty] | big drop in ventilation when add new hvac
Warehouse | 0 - Prototype | run/Prototype Row B/datapoint_59c942e553ff6b03c8620183 | Boise Air Terminal Uo | 1178560 | 52044.9 | 22.6451 | 1345 | 44.5 | 137.25 | 5.5 | 803152 | 375411 | 0 | 0 | 0 | 69.7761 | 463274 | 116837 | 115861 | 0 | 16217.2 | 0 | 375411 | 13563.3 | 77398.7 | 0 | 0 | 0 | 0 | 0 |  | 135772 | 34241.7 | 33955.6 | 0 | 4752.78 | 0 | 0 | 3975 | 22683.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3754.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 463277 | 115858 | 0 | 3923.68 | 2536.63 | 14244.1 | 142299 | 235049 | 183357 | 517140 | 205933 | 27643.5 | 799446 | 287708 | 69231.4 | 581878
Warehouse | 1 - Prototype-NewHvac | run/Prototype Row B/datapoint_59c942ed53ff6b03c8620193 | Boise Air Terminal Uo | 1160480 | 52044.9 | 22.2976 | 1873.25 | 176.5 | 119 | 5.75 | 777305 | 383165 | 0 | 0 | 0 | 70.9481 | 463274 | 116837 | 115861 | 0 | 16217.2 | 0 | 386406 | 12729.2 | 49144.3 | 0 | 0 | 0 | 0 | 0 |  | 135772 | 34241.7 | 33955.6 | 0 | 4752.78 | 0 | 950 | 3730.56 | 14402.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3832.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 463277 | 115858 | 0 | 3923.43 | 2619.25 | 16138.6 | 135062 | 235536 | 183359 | 517328 | 209041 | 71723 | 792579 | 288509 | 69284.1 | 582439
Warehouse | 2 - Prototype-NewHvacLoadsConstSch | run/Prototype Row B/datapoint_59c942f553ff6b03c86201a3 | Boise Air Terminal Uo | 895090 | 52044.9 | 17.1984 | 864.75 | 275.75 | 67 | 14 | 773883 | 121207 | 0 | 0 | 0 | 71.4196 | 463274 | 119292 | 115861 | 0 | 14378.4 | 0 | 121567 | 22264.2 | 38452.9 | 0 | 0 | 0 | 0 | 0 |  | 135772 | 34961.1 | 33955.6 | 0 | 4213.89 | 0 | 105.556 | 6525 | 11269.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1212.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 463277 | 115858 | 0 | 3797.17 | 3185.93 | 11533.1 | 547908 | 205869 | 174131 | 496912 | 336794 | 35451.5 | 448472 | 389732 | 84959.3 | 775657
Warehouse | 3b - Typical-Bar-Sliced | run/Prototype Row B/datapoint_59c9430753ff6b03c86201b3 | Boise Air Terminal Uo | 1351960 | 52044 | 25.9772 | 2967.25 | 1960.75 | 109.5 | 6.75 | 1073630 | 278326 | 0 | 0 | 0 | 114.016 | 463265 | 120344 | 115861 | 0 | 0 | 0 | 283407 | 130979 | 238101 | 0 | 0 | 0 | 0 | 0 |  | 135769 | 35269.4 | 33955.6 | 0 | 0 | 0 | 1488.89 | 38386.1 | 69780.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2783.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 463269 | 115858 | 0 | 3708.99 | 3124.31 | 5432.07 | 667877 | 14973.7 | 1634140 | 329068 | 366671 | 32008.7 | 1062970 | 106477 | 742515 | 778693
Warehouse | 4b - Typical-Bar-Blend | run/Prototype Row B/datapoint_59c9431053ff6b03c86201c3 | Boise Air Terminal Uo | 922956 | 52044 | 17.7341 | 758.25 | 115.25 | 69.75 | 54.5 | 783238 | 139718 | 0 | 0 | 0 | 59.5968 | 463265 | 120344 | 115861 | 0 | 0 | 0 | 140912 | 9070.61 | 73503.2 | 0 | 0 | 0 | 0 | 0 |  | 135769 | 35269.4 | 33955.6 | 0 | 0 | 0 | 350 | 2658.33 | 21541.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1397.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 463269 | 115858 | 0 | 3283.54 | 0 | 381.628 | 840845 | 6935.4 | 1534890 | 311390 | 377841 | 13037.1 | 1174110 | 102768 | 677401 | 746476
Warehouse | 4c - Typical-Urban-Blend | run/Prototype Row B/datapoint_59c9432b53ff6b03c86201d5 | Boise Air Terminal Uo | 729649 | 49498.6 | 14.7408 | 76.25 | 0 | 12.25 | 0 | 699413 | 30225.9 | 0 | 0 | 0 | 52.4869 | 440612 | 120344 | 110193 | 0 | 0 | 0 | 30595.5 | 246.432 | 27647.8 | 0 | 0 | 0 | 0 | 0 |  | 129131 | 35269.4 | 32294.4 | 0 | 0 | 0 | 108.333 | 72.2222 | 8102.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302.317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440611 | 110191 | 0 | 3245.5 | 0 | 267.043 | 847858 | 88833.8 | 854250 | 293367 | 324524 | 4285.71 | 919083 | 260077 | 316276 | 673119
Warehouse | 4d - Prototype-Prototype-Blend | run/Prototype Row B/datapoint_59c991be45b421004abe3ab6 | Boise Air Terminal Uo | 772803 | 52044.9 | 14.8488 | 1 | 0 | 0.75 | 0 | 742510 | 30292.2 | 0 | 0 | 0 | 54.9545 | 463274 | 119292 | 115861 | 0 | 14378.4 | 0 | 30292.2 | 47.3909 | 29657.2 | 0 | 0 | 0 | 0 | 0 |  | 135772 | 34961.1 | 33955.6 | 0 | 4213.89 | 0 | 0 | 13.8889 | 8691.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302.981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 463277 | 115858 | 0 | 4076.28 | 0 | 7639.06 | 632637 | 206550 | 174752 | 499074 | 323782 | 76.615 | 465691 | 381209 | 83179.2 | 766180
| bonus - 0 ot 2 error as single step | [15 empty] | 0 | 2455 | 0 | 0 | 1838.8 | 0 | 253844 | 8700.9 | 38945.8 | 0 | 0 | 0 | 0 | 0 | 25.95%
Warehouse | 0 - Prototype¦1 - Prototype-NewHvac |  | Boise Air Terminal Uo | 18080 | 0 | 0.3475 | 528.25 | 132 | 18.25 | 0.25 | 25847 | 7754 | 0 | 0 | 0 | 1.172 | 0% | 0% | 0% | 0% | 0% | 0% | 0.9329% | 0.07077% | 2.397% | 0% | 0% | 0% | 0% | 0% | 3.401% | 0 | 0 | 0 | 0 | 0 | 0 | 950 | 244.44 | 8280.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 82.62 | 1894.5 | 7237 | 487 | 2 | 188 | 3108 | 44079.5 | 6867 | 801 | 52.7 | 561
Warehouse | 1 - Prototype-NewHvac¦2 - Prototype-NewHvacLoadsConstSch |  | Boise Air Terminal Uo | 265390 | 0 | 5.0992 | 1008.5 | 99.25 | 52 | 8.25 | 3422 | 261958 | 0 | 0 | 0 | 0.4715 | 0% | 0.2116% | 0% | 0% | 0.1585% | 0% | 22.82% | 0.8216% | 0.9213% | 0% | 0% | 0% | 0% | 0% | 24.93% | 0 | 719.4 | 0 | 0 | 538.89 | 0 | 844.444 | 2794.44 | 3133.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2620.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126.26 | 566.68 | 4605.5 | 412846 | 29667 | 9228 | 20416 | 127753 | 36271.5 | 344107 | 101223 | 15675.2 | 193218
Warehouse | 2 - Prototype-NewHvacLoadsConstSch¦3b - Typical-Bar-Sliced |  | Boise Air Terminal Uo | 456870 | 0.9 | 8.7788 | 2102.5 | 1685 | 42.5 | 7.25 | 299747 | 157119 | 0 | 0 | 0 | 42.5964 | 0.001005% | 0.1175% | 0% | 0% | 1.606% | 0% | 18.08% | 12.15% | 22.3% | 0% | 0% | 0% | 0% | 0% | 54.26% | 3 | 308.3 | 0 | 0 | 4213.89 | 0 | 1383.334 | 31861.1 | 58511.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1571.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 88.18 | 61.62 | 6101.03 | 119969 | 190895.3 | 1460009 | 167844 | 29877 | 3442.8 | 614498 | 283255 | 657555.7 | 3036
Warehouse | 2 - Prototype-NewHvacLoadsConstSch¦4b - Typical-Bar-Blend |  | Boise Air Terminal Uo | 27866 | 0.9 | 0.5357 | 106.5 | 160.5 | 2.75 | 40.5 | 9355 | 18511 | 0 | 0 | 0 | 11.8228 | 0.001005% | 0.1175% | 0% | 0% | 1.606% | 0% | 2.161% | 1.474% | 3.916% | 0% | 0% | 0% | 0% | 0% | 9.276% | 3 | 308.3 | 0 | 0 | 4213.89 | 0 | 244.444 | 3866.67 | 10272.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 513.63 | 3185.93 | 11151.472 | 292937 | 198933.6 | 1360759 | 185522 | 41047 | 22414.4 | 725638 | 286964 | 592441.7 | 29181
Warehouse | 2 - Prototype-NewHvacLoadsConstSch¦4c - Typical-Urban-Blend |  | Boise Air Terminal Uo | 165441 | 2546.3 | 2.4576 | 788.5 | 275.75 | 54.75 | 14 | 74470 | 90981.1 | 0 | 0 | 0 | 18.9327 | 2.532% | 0.1175% | 0.6332% | 0% | 1.606% | 0% | 10.16% | 2.46% | 1.207% | 0% | 0% | 0% | 0% | 0% | 18.72% | 6641 | 308.3 | 1661.2 | 0 | 4213.89 | 0 | 2.777 | 6452.7778 | 3166.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 909.983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22666 | 5667 | 0 | 551.67 | 3185.93 | 11266.057 | 299950 | 117035.2 | 680119 | 203545 | 12270 | 31165.79 | 470611 | 129655 | 231316.7 | 102538
Warehouse | 2 - Prototype-NewHvacLoadsConstSch¦4d - Prototype-Prototype-Blend |  | Boise Air Terminal Uo | 122287 | 0 | 2.3496 | 863.75 | 275.75 | 66.25 | 14 | 31373 | 90914.8 | 0 | 0 | 0 | 16.4651 | 0% | 0% | 0% | 0% | 0% | 0% | 10.2% | 2.482% | 0.9827% | 0% | 0% | 0% | 0% | 0% | 13.66% | 0 | 0 | 0 | 0 | 0 | 0 | 105.556 | 6511.1111 | 2577.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 909.319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279.11 | 3185.93 | 3894.04 | 84729 | 681 | 621 | 2162 | 13012 | 35374.885 | 17219 | 8523 | 1780.1 | 9477
chart | [19 empty] | why large drop on heating when add in loads, and why larger envelope loads on bars (ah, wwr is based on office, not warehosue)
building_type | [15 empty] | building type | end use interior lighting | end use exterior lighting | end use interior equipment | end use exterior equipment | end use water systems | end use refrigeration | end use heating | end use cooling | end use fans | end use pumps | end use heat rejection | end use humidification | end use heat recovery | end use generators | sum of end use errors as fraction of total consumpiton
SecondarySchool | 0 - Prototype¦1 - Prototype-NewHvac | [14 empty] | SecondarySchool | 0% | 0% | 0% | 0% | 0.00442% | 0.001245% | 0.7565% | 0.09674% | 1.329% | 1.82% | 0.5216% | 0% | 2.053% | 0% | 6.582%
PrimarySchool | 0 - Prototype¦1 - Prototype-NewHvac | [14 empty] | PrimarySchool | 0% | 0% | 0% | 0% | 0.0001552% | 0.001473% | 15.7% | 0.8913% | 1.753% | 0.05671% | 0% | 0% | 0.004085% | 0% | 18.4%
FullServiceRestaurant | 0 - Prototype¦1 - Prototype-NewHvac | [14 empty] | FullServiceRestaurant | 0% | 0% | 0% | 0% | 0% | 0.005937% | 4.815% | 0.2945% | 3.161% | 0% | 0% | 0% | 0% | 0% | 8.276%
QuickServiceRestaurant | 0 - Prototype¦1 - Prototype-NewHvac | [14 empty] | QuickServiceRestaurant | 0% | 0% | 0% | 0% | 0% | 0.01498% | 1.143% | 0.3692% | 1.783% | 0% | 0% | 0% | 0% | 0% | 3.31%
SmallOffice | 0 - Prototype¦1 - Prototype-NewHvac | [14 empty] | SmallOffice | 0% | 0% | 0% | 0% | 0% | 0% | 14.8% | 0.02158% | 16.88% | 0% | 0% | 0% | 0% | 0% | 31.7%
MediumOffice | 0 - Prototype¦1 - Prototype-NewHvac | [14 empty] | MediumOffice | 0% | 0% | 0% | 0% | 0.0007205% | 0% | 14.18% | 1.467% | 7.618% | 0% | 0% | 0% | 0% | 0% | 23.26%
LargeOffice | 0 - Prototype¦1 - Prototype-NewHvac | [14 empty] | LargeOffice | 0% | 0% | 0% | 0% | 0.0005189% | 0% | 2.06% | 11.87% | 0.3272% | 1.223% | 0.3879% | 6.27% | 2.421% | 0% | 24.56%
LargeHotel | 0 - Prototype¦1 - Prototype-NewHvac | [14 empty] | LargeHotel | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
MidriseApartment | 0 - Prototype¦1 - Prototype-NewHvac | [14 empty] | MidriseApartment | 0% | 0% | 0% | 0% | 0% | 0% | 5.08% | 1.85% | 15.09% | 0.01293% | 0% | 0% | 0% | 0% | 22.04%
HighriseApartment | 0 - Prototype¦1 - Prototype-NewHvac | [14 empty] | HighriseApartment | 0% | 0% | 0% | 0% | 0.0004292% | 0% | 2.004% | 0.6594% | 14.34% | 0.9692% | 0.8044% | 0% | 0% | 0% | 18.78%
StripMall | 0 - Prototype¦1 - Prototype-NewHvac | [14 empty] | StripMall | 0% | 0% | 0% | 0% | 0.001008% | 0% | 3.233% | 0.7399% | 3.383% | 0% | 0% | 0% | 0% | 0% | 7.357%
Retail | 0 - Prototype¦1 - Prototype-NewHvac | [14 empty] | Retail | 0% | 0% | 0% | 0% | 0% | 0% | 3.419% | 1.405% | 1.65% | 0% | 0% | 0% | 0% | 0% | 6.474%
Hospital | 0 - Prototype¦1 - Prototype-NewHvac | [14 empty] | Hospital | 0% | 0% | 0% | 0% | 2.883e-05% | 0.02265% | 9.317% | 4.753% | 2.745% | 0.52% | 0.6723% | 5.764% | 0% | 0% | 23.79%
Outpatient | 0 - Prototype¦1 - Prototype-NewHvac | [14 empty] | Outpatient | 0% | 0% | 0% | 0% | 0.0001541% | 0% | 14.94% | 1.946% | 2.609% | 0.3053% | 0% | 2.866% | 0% | 0% | 22.66%
Warehouse | 0 - Prototype¦1 - Prototype-NewHvac | [14 empty] | Warehouse | 0% | 0% | 0% | 0% | 0% | 0% | 0.9329% | 0.07077% | 2.397% | 0% | 0% | 0% | 0% | 0% | 3.401%
building_type | [15 empty] | building type | end use interior lighting | end use exterior lighting | end use interior equipment | end use exterior equipment | end use water systems | end use refrigeration | end use heating | end use cooling | end use fans | end use pumps | end use heat rejection | end use humidification | end use heat recovery | end use generators | sum of end use errors as fraction of total consumpiton
SecondarySchool | 1 - Prototype-NewHvac¦2 - Prototype-NewHvacLoadsConstSch | [14 empty] | SecondarySchool | 0% | 2.144% | 0.02541% | 0% | 0.5472% | 0.0008386% | 3.482% | 0.6368% | 0.4649% | 0.1236% | 0.02019% | 0% | 0.12% | 0% | 7.565%
PrimarySchool | 1 - Prototype-NewHvac¦2 - Prototype-NewHvacLoadsConstSch | [14 empty] | PrimarySchool | 0% | 2.015% | 0% | 0% | 0.8601% | 0.002404% | 4.239% | 0.8117% | 0.2734% | 0.001202% | 0% | 0% | 0.01282% | 0% | 8.215%
FullServiceRestaurant | 1 - Prototype-NewHvac¦2 - Prototype-NewHvacLoadsConstSch | [14 empty] | FullServiceRestaurant | 0% | 0.1214% | 1.527% | 0% | 0.6172% | 0.02479% | 21.46% | 0.5449% | 9.182% | 0.009206% | 0% | 0% | 1.702% | 0% | 35.19%
QuickServiceRestaurant | 1 - Prototype-NewHvac¦2 - Prototype-NewHvacLoadsConstSch | [14 empty] | QuickServiceRestaurant | 0% | 0.5292% | 2.78% | 0% | 0.3796% | 0.01869% | 12.12% | 0.5859% | 7.832% | 0% | 0% | 0% | 0% | 0% | 24.25%
SmallOffice | 1 - Prototype-NewHvac¦2 - Prototype-NewHvacLoadsConstSch | [14 empty] | SmallOffice | 0% | 1.894% | 0% | 0% | 1.301% | 0% | 1.678% | 0.5965% | 0.4916% | 0% | 0% | 0% | 0% | 0% | 5.962%
MediumOffice | 1 - Prototype-NewHvac¦2 - Prototype-NewHvacLoadsConstSch | [14 empty] | MediumOffice | 0% | 1.032% | 2.772% | 0% | 1.158% | 0% | 1.721% | 0.67% | 0.08985% | 0% | 0% | 0% | 0% | 0% | 7.444%
LargeOffice | 1 - Prototype-NewHvac¦2 - Prototype-NewHvacLoadsConstSch | [14 empty] | LargeOffice | 0% | 3.594% | 3.731% | 0% | 0.5557% | 0% | 1.622% | 0.1354% | 0.01763% | 0.02971% | 0.003111% | 0% | 0% | 0% | 9.689%
LargeHotel | 1 - Prototype-NewHvac¦2 - Prototype-NewHvacLoadsConstSch | [14 empty] | LargeHotel | Re-run after 2.3.0 comes out
MidriseApartment | 1 - Prototype-NewHvac¦2 - Prototype-NewHvacLoadsConstSch | [14 empty] | MidriseApartment | 0% | 6.815% | 0.00278% | 0% | 7.371% | 0% | 0.08965% | 0.7457% | 3.08% | 0% | 0% | 0% | 0% | 0% | 18.1%
HighriseApartment | 1 - Prototype-NewHvac¦2 - Prototype-NewHvacLoadsConstSch | [14 empty] | HighriseApartment | 0% | 0.8878% | 1.487% | 0% | 1.002% | 0% | 0.1335% | 0.1412% | 0.3328% | 0% | 0% | 0% | 0% | 0% | 3.984%
StripMall | 1 - Prototype-NewHvac¦2 - Prototype-NewHvacLoadsConstSch | [14 empty] | StripMall | 0% | 2.486% | 0% | 0% | 2.809% | 0% | 5.663% | 0.5464% | 3.253% | 0% | 0% | 0% | 0% | 0% | 14.76%
Retail | 1 - Prototype-NewHvac¦2 - Prototype-NewHvacLoadsConstSch | [14 empty] | Retail | 0% | 0.3176% | 0% | 0% | 0% | 0% | 1.069% | 1.118% | 7.176% | 0% | 0% | 0% | 0% | 0% | 9.68%
Hospital | 1 - Prototype-NewHvac¦2 - Prototype-NewHvacLoadsConstSch | [14 empty] | Hospital | 0% | 7.42% | 5.023% | 0% | 1.51% | 3.026e-05% | 2.6% | 0.2437% | 0.2045% | 0.0354% | 0.005449% | 0% | 0% | 0% | 17.04%
Outpatient | 1 - Prototype-NewHvac¦2 - Prototype-NewHvacLoadsConstSch | [14 empty] | Outpatient | 0.03606% | 0.4556% | 2.095% | 0% | 0.6892% | 0% | 1.15% | 0.1922% | 0.7838% | 0% | 0% | 0% | 0% | 0% | 5.401%
Warehouse | 1 - Prototype-NewHvac¦2 - Prototype-NewHvacLoadsConstSch | [14 empty] | Warehouse | 0% | 0.2116% | 0% | 0% | 0.1585% | 0% | 22.82% | 0.8216% | 0.9213% | 0% | 0% | 0% | 0% | 0% | 24.93%
building_type | [15 empty] | building type | end use interior lighting | end use exterior lighting | end use interior equipment | end use exterior equipment | end use water systems | end use refrigeration | end use heating | end use cooling | end use fans | end use pumps | end use heat rejection | end use humidification | end use heat recovery | end use generators | sum of end use errors as fraction of total consumpiton
SecondarySchool | 2 - Prototype-NewHvacLoadsConstSch¦3b - Typical-Bar-Sliced | [14 empty] | SecondarySchool | 6.092e-05% | 0.07622% | 0.007859% | 0% | 0.1886% | 0.5137% | 20.83% | 0.249% | 2.488% | 0.03851% | 0.01357% | 0% | 0.3572% | 0% | 24.76%
PrimarySchool | 2 - Prototype-NewHvacLoadsConstSch¦3b - Typical-Bar-Sliced | [14 empty] | PrimarySchool | 0.008923% | 0.005631% | 0.008129% | 0% | 0.5405% | 0.9194% | 2.734% | 1.184% | 5.406% | 0% | 0% | 0% | 0.3492% | 0% | 11.16%
FullServiceRestaurant | 2 - Prototype-NewHvacLoadsConstSch¦3b - Typical-Bar-Sliced | [14 empty] | FullServiceRestaurant | 0.003535% | 0.001018% | 0.007124% | 0% | 1.352% | 1.873% | 24.3% | 1.445% | 3.904% | 0% | 0% | 0% | 2.441% | 0% | 35.33%
QuickServiceRestaurant | 2 - Prototype-NewHvacLoadsConstSch¦3b - Typical-Bar-Sliced | [14 empty] | QuickServiceRestaurant | 0.009963% | 0.004986% | 0.09219% | 0% | 0.9153% | 3.132% | 11.74% | 1.752% | 2.233% | 0% | 0% | 0% | 0% | 0% | 19.88%
SmallOffice | 2 - Prototype-NewHvacLoadsConstSch¦3b - Typical-Bar-Sliced | [14 empty] | SmallOffice | 0.009462% | 0.006297% | 0.00633% | 0% | 5.69% | 0% | 2.416% | 2.056% | 2.608% | 0% | 0% | 0% | 0% | 0% | 12.79%
MediumOffice | 2 - Prototype-NewHvacLoadsConstSch¦3b - Typical-Bar-Sliced | [14 empty] | MediumOffice | 0.0007603% | 0.1339% | 0.00116% | 0% | 1.654% | 0% | 2.638% | 0.5537% | 2.052% | 0% | 0% | 0% | 0% | 0% | 7.034%
LargeOffice | 2 - Prototype-NewHvacLoadsConstSch¦3b - Typical-Bar-Sliced | [14 empty] | LargeOffice | 8.806e-05% | 0.01079% | 0.01431% | 0% | 0.1823% | 0% | 0.4615% | 2.157% | 1.081% | 0.2051% | 0.1368% | 0% | 2.964% | 0% | 7.212%
LargeHotel | 2 - Prototype-NewHvacLoadsConstSch¦3b - Typical-Bar-Sliced | [14 empty] | LargeHotel | Re-run after 2.3.0 comes out
MidriseApartment | 2 - Prototype-NewHvacLoadsConstSch¦3b - Typical-Bar-Sliced | [14 empty] | MidriseApartment | 0.001681% | 0% | 0.0003981% | 0% | 0.4612% | 0% | 0.3253% | 1.61% | 2.833% | 0.0008385% | 0% | 0% | 0% | 0% | 5.232%
HighriseApartment | 2 - Prototype-NewHvacLoadsConstSch¦3b - Typical-Bar-Sliced | [14 empty] | HighriseApartment | 0.001258% | 0% | 0.0003755% | 0% | 1.439% | 0% | 0.4601% | 3.274% | 6.92% | 0.001246% | 0% | 0% | 0% | 0% | 12.1%
StripMall | 2 - Prototype-NewHvacLoadsConstSch¦3b - Typical-Bar-Sliced | [14 empty] | StripMall | 0.005028% | 0.0005323% | 0.001124% | 0% | 2.696% | 0% | 5.092% | 0.1856% | 1.476% | 0% | 0% | 0% | 0% | 0% | 9.456%
Retail | 2 - Prototype-NewHvacLoadsConstSch¦3b - Typical-Bar-Sliced | [14 empty] | Retail | 0% | 0% | 0.002131% | 0% | 3.117% | 0% | 4.253% | 0.4571% | 1.803% | 0% | 0% | 0% | 0% | 0% | 9.632%
Hospital | 2 - Prototype-NewHvacLoadsConstSch¦3b - Typical-Bar-Sliced | [14 empty] | Hospital | 0.4238% | 0.022% | 3.407% | 0% | 0.08266% | 0.4006% | 2.152% | 0.1513% | 0.05189% | 0.04999% | 0.06522% | 0% | 0% | 0% | 6.807%
Outpatient | 2 - Prototype-NewHvacLoadsConstSch¦3b - Typical-Bar-Sliced | [14 empty] | Outpatient | 0.1658% | 0.0838% | 0.9267% | 0% | 0.7658% | 0% | 3.394% | 0.2036% | 0.159% | 0.0001949% | 0% | 0% | 0% | 0% | 5.699%
Warehouse | 2 - Prototype-NewHvacLoadsConstSch¦3b - Typical-Bar-Sliced | [14 empty] | Warehouse | 0.001005% | 0.1175% | 0% | 0% | 1.606% | 0% | 18.08% | 12.15% | 22.3% | 0% | 0% | 0% | 0% | 0% | 54.26%
Note: Full Surface Restaurant is 35%, Warehouse is 54%
building_type | [15 empty] | building type | end use interior lighting | end use exterior lighting | end use interior equipment | end use exterior equipment | end use water systems | end use refrigeration | end use heating | end use cooling | end use fans | end use pumps | end use heat rejection | end use humidification | end use heat recovery | end use generators | sum of end use errors as fraction of total consumpiton
SecondarySchool | 2 - Prototype-NewHvacLoadsConstSch¦4b - Typical-Bar-Blend | [14 empty] | SecondarySchool | 6.092e-05% | 0.07622% | 0.007859% | 0% | 0.1887% | 0.5137% | 8.096% | 1.004% | 0.5821% | 0.1807% | 0.0004624% | 0% | 0.9581% | 0% | 11.61%
PrimarySchool | 2 - Prototype-NewHvacLoadsConstSch¦4b - Typical-Bar-Blend | [14 empty] | PrimarySchool | 0.008923% | 0.005631% | 0.008129% | 0% | 0.5407% | 0.9194% | 1.799% | 0.03684% | 4.608% | 0% | 0% | 0% | 1.042% | 0% | 8.968%
FullServiceRestaurant | 2 - Prototype-NewHvacLoadsConstSch¦4b - Typical-Bar-Blend | [14 empty] | FullServiceRestaurant | 0.003535% | 0.001018% | 0.007124% | 0% | 1.352% | 1.873% | 19.54% | 1.157% | 3.951% | 0% | 0% | 0% | 2.441% | 0% | 30.32%
QuickServiceRestaurant | 2 - Prototype-NewHvacLoadsConstSch¦4b - Typical-Bar-Blend | [14 empty] | QuickServiceRestaurant | 0.009963% | 0.004986% | 0.09219% | 0% | 0.9153% | 3.132% | 9.998% | 2.14% | 2.081% | 0% | 0% | 0% | 0% | 0% | 18.37%
SmallOffice | 2 - Prototype-NewHvacLoadsConstSch¦4b - Typical-Bar-Blend | [14 empty] | SmallOffice | 0.009462% | 0.006297% | 0.00633% | 0% | 5.69% | 0% | 2.725% | 2.059% | 2.861% | 0% | 0% | 0% | 0% | 0% | 13.36%
MediumOffice | 2 - Prototype-NewHvacLoadsConstSch¦4b - Typical-Bar-Blend | [14 empty] | MediumOffice | 0.0007603% | 0.1339% | 0.00116% | 0% | 1.654% | 0% | 2.433% | 0.05838% | 2.236% | 0% | 0% | 0% | 0% | 0% | 6.517%
LargeOffice | 2 - Prototype-NewHvacLoadsConstSch¦4b - Typical-Bar-Blend | [14 empty] | LargeOffice | 8.806e-05% | 0.01079% | 0.01431% | 0% | 0.1824% | 0% | 7.814% | 3.262% | 1.076% | 0.04385% | 0.07707% | 0% | 0.04832% | 0% | 12.53%
LargeHotel | 2 - Prototype-NewHvacLoadsConstSch¦4b - Typical-Bar-Blend | [14 empty] | LargeHotel | Re-run after 2.3.0 comes out
MidriseApartment | 2 - Prototype-NewHvacLoadsConstSch¦4b - Typical-Bar-Blend | [14 empty] | MidriseApartment | 0.001681% | 0% | 0.0003981% | 0% | 0.4612% | 0% | 1.321% | 0.2159% | 0.2402% | 0.001677% | 0% | 0% | 0% | 0% | 2.242%
HighriseApartment | 2 - Prototype-NewHvacLoadsConstSch¦4b - Typical-Bar-Blend | [14 empty] | HighriseApartment | 0.001258% | 0% | 0.0003755% | 0% | 1.439% | 0% | 1.477% | 1.612% | 2.599% | 0.002135% | 0% | 0% | 0% | 0% | 7.13%
StripMall | 2 - Prototype-NewHvacLoadsConstSch¦4b - Typical-Bar-Blend | [14 empty] | StripMall | 0.005028% | 0.0005323% | 0.001124% | 0% | 2.696% | 0% | 1.202% | 0.4042% | 0.855% | 0% | 0% | 0% | 0% | 0% | 5.163%
Retail | 2 - Prototype-NewHvacLoadsConstSch¦4b - Typical-Bar-Blend | [14 empty] | Retail | 0% | 0% | 0.002131% | 0% | 3.117% | 0% | 3.089% | 0.3098% | 2.842% | 0% | 0% | 0% | 0% | 0% | 9.36%
Hospital | 2 - Prototype-NewHvacLoadsConstSch¦4b - Typical-Bar-Blend | [14 empty] | Hospital | 0.4238% | 0.022% | 3.407% | 0% | 0.08266% | 0.4006% | 10.71% | 2.035% | 5.2% | 0.5291% | 0.09108% | 0% | 0% | 0% | 22.9%
Outpatient | 2 - Prototype-NewHvacLoadsConstSch¦4b - Typical-Bar-Blend | [14 empty] | Outpatient | 0.1658% | 0.0838% | 0.9267% | 0% | 0.7664% | 0% | 5.646% | 1.804% | 3.473% | 0.0001949% | 0% | 0% | 0% | 0% | 12.87%
Warehouse | 2 - Prototype-NewHvacLoadsConstSch¦4b - Typical-Bar-Blend | [14 empty] | Warehouse | 0.001005% | 0.1175% | 0% | 0% | 1.606% | 0% | 2.161% | 1.474% | 3.916% | 0% | 0% | 0% | 0% | 0% | 9.276%
building_type | [15 empty] | building type | end use interior lighting | end use exterior lighting | end use interior equipment | end use exterior equipment | end use water systems | end use refrigeration | end use heating | end use cooling | end use fans | end use pumps | end use heat rejection | end use humidification | end use heat recovery | end use generators | sum of end use errors as fraction of total consumpiton
SecondarySchool | 2 - Prototype-NewHvacLoadsConstSch¦4c - Typical-Urban-Blend | [14 empty] | SecondarySchool | 4.178% | 0.07622% | 3.71% | 0% | 0.1887% | 0.5137% | 4.08% | 1.467% | 4.268% | 0.2981% | 0.01836% | 0% | 0.9577% | 0% | 19.76%
PrimarySchool | 2 - Prototype-NewHvacLoadsConstSch¦4c - Typical-Urban-Blend | [14 empty] | PrimarySchool | 0.0009914% | 0.005631% | 0.01923% | 0% | 0.5407% | 0.9194% | 4.551% | 2.176% | 1.013% | 0% | 0% | 0% | 0.5706% | 0% | 9.796%
FullServiceRestaurant | 2 - Prototype-NewHvacLoadsConstSch¦4c - Typical-Urban-Blend | [14 empty] | FullServiceRestaurant | 0.0005357% | 0.001018% | 0.01168% | 0% | 1.353% | 1.873% | 18.64% | 1.479% | 2.463% | 0% | 0% | 0% | 2.441% | 0% | 28.27%
QuickServiceRestaurant | 2 - Prototype-NewHvacLoadsConstSch¦4c - Typical-Urban-Blend | [14 empty] | QuickServiceRestaurant | 0% | 0.004986% | 0.00333% | 0% | 0.9153% | 3.132% | 5.809% | 1.493% | 1.742% | 0% | 0% | 0% | 0% | 0% | 13.1%
SmallOffice | 2 - Prototype-NewHvacLoadsConstSch¦4c - Typical-Urban-Blend | [14 empty] | SmallOffice | 0.003132% | 0.006297% | 0% | 0% | 5.69% | 0% | 4.97% | 1.645% | 10.17% | 0% | 0% | 0% | 0% | 0% | 22.48%
MediumOffice | 2 - Prototype-NewHvacLoadsConstSch¦4c - Typical-Urban-Blend | [14 empty] | MediumOffice | 0.0004001% | 0.1339% | 0.0007603% | 0% | 1.654% | 0% | 2.68% | 0.6049% | 7.649% | 0% | 0% | 0% | 0% | 0% | 12.72%
LargeOffice | 2 - Prototype-NewHvacLoadsConstSch¦4c - Typical-Urban-Blend | [14 empty] | LargeOffice | 0.0001761% | 0.01079% | 0.01475% | 0% | 0.1824% | 0% | 9.33% | 3.094% | 3.701% | 0.4301% | 0.07851% | 0% | 2.964% | 0% | 19.81%
LargeHotel | 2 - Prototype-NewHvacLoadsConstSch¦4c - Typical-Urban-Blend | [14 empty] | LargeHotel | Re-run after 2.3.0 comes out
MidriseApartment | 2 - Prototype-NewHvacLoadsConstSch¦4c - Typical-Urban-Blend | [14 empty] | MidriseApartment | 0.006281% | 0% | 0.03437% | 0% | 0.4612% | 0% | 2.009% | 0.7978% | 0.8167% | 0.001677% | 0% | 0% | 0% | 0% | 4.127%
HighriseApartment | 2 - Prototype-NewHvacLoadsConstSch¦4c - Typical-Urban-Blend | [14 empty] | HighriseApartment | 0.002121% | 0% | 0.01483% | 0% | 1.439% | 0% | 2.199% | 0.4756% | 1.464% | 0.002313% | 0% | 0% | 0% | 0% | 5.597%
StripMall | 2 - Prototype-NewHvacLoadsConstSch¦4c - Typical-Urban-Blend | [14 empty] | StripMall | 0.001715% | 0.0005323% | 0% | 0% | 2.696% | 0% | 3.434% | 0.3549% | 6.058% | 0% | 0% | 0% | 0% | 0% | 12.54%
Retail | 2 - Prototype-NewHvacLoadsConstSch¦4c - Typical-Urban-Blend | [14 empty] | Retail | 0.006392% | 0% | 0.004261% | 0% | 3.117% | 0% | 4.313% | 0.8987% | 2.342% | 0% | 0% | 0% | 0% | 0% | 10.68%
Hospital | 2 - Prototype-NewHvacLoadsConstSch¦4c - Typical-Urban-Blend | [14 empty] | Hospital | 0.4235% | 0.022% | 3.406% | 0% | 0.08266% | 0.4006% | 11.9% | 2.605% | 8.662% | 0.6124% | 0.08664% | 0% | 0% | 0% | 28.2%
Outpatient | 2 - Prototype-NewHvacLoadsConstSch¦4c - Typical-Urban-Blend | [14 empty] | Outpatient | 1.19% | 0.0838% | 4.183% | 0% | 0.7664% | 0% | 8.332% | 1.103% | 5.352% | 0.0001949% | 0% | 0% | 0% | 0% | 21.01%
Warehouse | 2 - Prototype-NewHvacLoadsConstSch¦4c - Typical-Urban-Blend | [14 empty] | Warehouse | 2.532% | 0.1175% | 0.6332% | 0% | 1.606% | 0% | 10.16% | 2.46% | 1.207% | 0% | 0% | 0% | 0% | 0% | 18.72%
Note: Since footprint is extruded for each above grade story, buildings which to not have full upper stories will show too much area, such as secondary school
building_type | [15 empty] | building type | end use interior lighting | end use exterior lighting | end use interior equipment | end use exterior equipment | end use water systems | end use refrigeration | end use heating | end use cooling | end use fans | end use pumps | end use heat rejection | end use humidification | end use heat recovery | end use generators | sum of end use errors as fraction of total consumpiton
SecondarySchool | 2 - Prototype-NewHvacLoadsConstSch¦4d - Prototype-Prototype-Blend | [14 empty] | SecondarySchool | 0% | 0% | 0% | 0% | 6.092e-05% | 0.03262% | 1.335% | 0.9941% | 0.7353% | 0.1908% | 0.01259% | 0% | 0.5941% | 0% | 3.895%
PrimarySchool | 2 - Prototype-NewHvacLoadsConstSch¦4d - Prototype-Prototype-Blend | [14 empty] | PrimarySchool | 0% | 0% | 0% | 0% | 0% | 0.04811% | 5.99% | 0.07838% | 0.6119% | 0% | 0% | 0% | 0.5706% | 0% | 7.299%
FullServiceRestaurant | 2 - Prototype-NewHvacLoadsConstSch¦4d - Prototype-Prototype-Blend | [14 empty] | FullServiceRestaurant | 0% | 0% | 0% | 0% | 0% | 0.02691% | 12.06% | 1.181% | 0.02641% | 0% | 0% | 0% | 2.441% | 0% | 15.73%
QuickServiceRestaurant | 2 - Prototype-NewHvacLoadsConstSch¦4d - Prototype-Prototype-Blend | [14 empty] | QuickServiceRestaurant | 0% | 0% | 0% | 0% | 0% | 0.01827% | 0.1396% | 0.8762% | 1.145% | 0% | 0% | 0% | 0% | 0% | 2.179%
SmallOffice | 2 - Prototype-NewHvacLoadsConstSch¦4d - Prototype-Prototype-Blend | [14 empty] | SmallOffice | 0% | 0% | 0% | 0% | 0% | 0% | 0.1358% | 0.03792% | 0.1453% | 0% | 0% | 0% | 0% | 0% | 0.319%
MediumOffice | 2 - Prototype-NewHvacLoadsConstSch¦4d - Prototype-Prototype-Blend | [14 empty] | MediumOffice | Need to address plenum zones to model this properly
LargeOffice | 2 - Prototype-NewHvacLoadsConstSch¦4d - Prototype-Prototype-Blend | [14 empty] | LargeOffice | Need to address plenum zones to model this properly
LargeHotel | 2 - Prototype-NewHvacLoadsConstSch¦4d - Prototype-Prototype-Blend | [14 empty] | LargeHotel | Re-run after 2.3.0 comes out
MidriseApartment | 2 - Prototype-NewHvacLoadsConstSch¦4d - Prototype-Prototype-Blend | [14 empty] | MidriseApartment | 0% | 0% | 0% | 0% | 0% | 0% | 0.9077% | 0.02433% | 0.1002% | 0.0008385% | 0% | 0% | 0% | 0% | 1.033%
HighriseApartment | 2 - Prototype-NewHvacLoadsConstSch¦4d - Prototype-Prototype-Blend | [14 empty] | HighriseApartment | 0% | 0% | 0% | 0% | 0.0003755% | 0% | 0.5518% | 0.006777% | 0.5039% | 0.0005338% | 0% | 0% | 0% | 0% | 1.063%
StripMall | 2 - Prototype-NewHvacLoadsConstSch¦4d - Prototype-Prototype-Blend | [14 empty] | StripMall | 0% | 0% | 0% | 0% | 0% | 0% | 2.821% | 0.007867% | 0.2192% | 0% | 0% | 0% | 0% | 0% | 3.048%
Retail | 2 - Prototype-NewHvacLoadsConstSch¦4d - Prototype-Prototype-Blend | [14 empty] | Retail | 0% | 0% | 0% | 0% | 0% | 0% | 0.2131% | 0.06274% | 0.09992% | 0% | 0% | 0% | 0% | 0% | 0.3758%
Hospital | 2 - Prototype-NewHvacLoadsConstSch¦4d - Prototype-Prototype-Blend | [14 empty] | Hospital | 0% | 0% | 0% | 0% | 0% | 0.01182% | 8.197% | 2.537% | 5.835% | 0.5143% | 0.05282% | 0% | 0% | 0% | 17.15%
Outpatient | 2 - Prototype-NewHvacLoadsConstSch¦4d - Prototype-Prototype-Blend | [14 empty] | Outpatient | 0% | 0% | 0% | 0% | 0.0009663% | 0% | 0.1686% | 1.309% | 0.4322% | 0% | 0% | 0% | 0% | 0% | 1.911%
Warehouse | 2 - Prototype-NewHvacLoadsConstSch¦4d - Prototype-Prototype-Blend | [14 empty] | Warehouse | 0% | 0% | 0% | 0% | 0% | 0% | 10.2% | 2.482% | 0.9827% | 0% | 0% | 0% | 0% | 0% | 13.66%
Note: Medium Office is 79%, Large office is 76% (expected cause is handeling of plenum zone)
[20 empty] | Multiple Space Types Sliced Bar | Whole Building Space Type Core and Perimeter Bar | Whole Building Space Type Extruded Footprint | Whole Building SpaceType Prototype Geometry
building_type | [18 empty] | building_type | 2 - Prototype-NewHvacLoadsConstSch¦3b - Typical-Bar-Sliced | 2 - Prototype-NewHvacLoadsConstSch¦4b - Typical-Bar-Blend | 2 - Prototype-NewHvacLoadsConstSch¦4c - Typical-Urban-Blend | 2 - Prototype-NewHvacLoadsConstSch¦4d - Prototype-Prototype-Blend
SecondarySchool | [18 empty] | SecondarySchool | 24.76% | 11.61% | 19.76% | 3.895%
PrimarySchool | [18 empty] | PrimarySchool | 11.16% | 8.968% | 9.796% | 7.299%
FullServiceRestaurant | [18 empty] | FullServiceRestaurant | 35.33% | 30.32% | 28.27% | 15.73%
QuickServiceRestaurant | [18 empty] | QuickServiceRestaurant | 19.88% | 18.37% | 13.1% | 2.179%
SmallOffice | [18 empty] | SmallOffice | 12.79% | 13.36% | 22.48% | 0.319%
MediumOffice | [18 empty] | MediumOffice | 7.034% | 6.517% | 12.72%
LargeOffice | [18 empty] | LargeOffice | 7.212% | 12.53% | 19.81%
LargeHotel | [18 empty] | LargeHotel
MidriseApartment | [18 empty] | MidriseApartment | 5.232% | 2.242% | 4.127% | 1.033%
HighriseApartment | [18 empty] | HighriseApartment | 12.1% | 7.13% | 5.597% | 1.063%
StripMall | [18 empty] | StripMall | 9.456% | 5.163% | 12.54% | 3.048%
Retail | [18 empty] | Retail | 9.632% | 9.36% | 10.68% | 0.3758%
Hospital | [18 empty] | Hospital | 6.807% | 22.9% | 28.2% | 17.15%
Outpatient | [18 empty] | Outpatient | 5.699% | 12.87% | 21.01% | 1.911%
Warehouse | [18 empty] | Warehouse | 54.26% | 9.276% | 18.72% | 13.66%
Note: Large hotel missing for all simplification methods
Note: Medium and Large office missing from 4d - Protottype-Prototype-Blend
building_type | [18 empty] | building_type | Prototype with New HVAC | Prototype with new HVAC, Const, Load, and Sch
SecondarySchool | [18 empty] | SecondarySchool | 6.582% | 13.69%
PrimarySchool | [18 empty] | PrimarySchool | 18.4% | 17.73%
FullServiceRestaurant | [18 empty] | FullServiceRestaurant | 8.276% | 36.08%
QuickServiceRestaurant | [18 empty] | QuickServiceRestaurant | 3.31% | 23.5%
SmallOffice | [18 empty] | SmallOffice | 31.7% | 38.25%
MediumOffice | [18 empty] | MediumOffice | 23.26% | 25.62%
LargeOffice | [18 empty] | LargeOffice | 24.56% | 35.33%
LargeHotel | [18 empty] | LargeHotel
MidriseApartment | [18 empty] | MidriseApartment | 22.04% | 33.73%
HighriseApartment | [18 empty] | HighriseApartment | 18.78% | 22.16%
StripMall | [18 empty] | StripMall | 7.357% | 20.22%
Retail | [18 empty] | Retail | 6.474% | 14.15%
Hospital | [18 empty] | Hospital | 23.79% | 33.53%
Outpatient | [18 empty] | Outpatient | 22.66% | 26.84%
Warehouse | [18 empty] | Warehouse | 3.401% | 3.401%
Note: Large hotel missing for all simplification methods